## RECTIFIERS
3 Phase Rectifiers |  |  |  |  | VERIFIER LES COEFFICIENT DES TRANSFOS AVEC DES MODELES EXISTANTS
| Vnom | Idc | #cel | VPC | Vmax | Vsec | Isec | Psec |  | P | Iprim | At Vac | CB1 | AWG | AWG | AWG | CB2 | SCR | VM | AM | fuse | TVS | ALARM
| (Vdc) | (Idc) |  | (Vdc) | (Vdc) | (Vac) | (Iac) | (Kva) |  | (Kva) | (Iac) | (Vac) | (Iac) | Prim | Sec | DC | (Idc) | Model | Scale | Scale | (A) |  | 5 RELAY
| Specs: |  |  |  |  | Transformer Sizing (3 Phase) |  |  |  | (Iac): Circuit Breaker Sizing; Scale: Wire Sizing | [7 empty] | Heat Dissipation |  | Environment |  | Fan Sizing | [7 empty] | Air Conditionner Sizing
| Output |  | Input |  |  | k6 rated-115deg C-50/60 Hz |  |  |  | (Iac): Primary Input; Prim: Secondary Output; (Idc): DC Output; Scale: Primary |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  | NEMA 3R | NEMA 12 | Fan Type | Fan CFM | Fan CFM | Fan CFM | Fan CFM | Encl.Size
| Vdc | Idc | Vpri | Ipri | 5 | Vsec l-n | Vsec l-l | 20 | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | Required |  | 100 | 200 | 100 | 200 | Model: | W | H | Depth | Surface | Required
| (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | (CFM) |  | QTY | QTY | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
| 600 | 600 | 480 | 582.1615 | 5 | 269.64 | 467.0302 | 20 | 597.6 | 484 | 30 | 756.81 | 800 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 669.4857 | 300MCM 2x | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 30.24 | 103183.1741 | 40 | 55 | 20 | 4257.792 | 5662.8634 | 4.7x4.7 | 44 | 22 | 58 | 30 | 450 | 24 | 30 | 16 | 19.3333 | 102820.6741
| 640 | 54 | 480 | 56.5322 | 5 | 287.616 | 498.1655 | 20 | 53.784 | 47 | 30 | 73.4919 | 80 | 30 | 69.9192 | 70 | 30 | 70.2 | 70 | 15 | 65.012 | #6 | 10 | 59.1624 | #8 | 10 | 59.4 | #8 | 2.928 | 9990.7518 | 40 | 55 | 20 | 412.2624 | 548.309 | 4.7x4.7 | 6 | 4 | 6 | 4 | 450 | 24 | 30 | 16 | 19.3333 | 9628.2518
| Specs: |  |  |  |  | Transformer Sizing (3 Phase) |  |  |  | (Iac): Circuit Breaker Sizing; Scale: Wire Sizing | [7 empty] | Heat Dissipation |  | Environment |  | Fan Sizing | [7 empty] | Air Conditionner Sizing | [5 empty] | Enclosure Type
# Stacks | Output |  | Input |  |  | k6 rated-115deg C-50/60 Hz |  |  |  | (Iac): Primary Input; Prim: Secondary Output; (Idc): DC Output; Scale: Primary |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  | NEMA 3R | NEMA 12 | Fan Type | Fan CFM | Fan CFM | Fan CFM | Fan CFM | Encl.Size | [5 empty] | NEMA 3R | NEMA 12 | NEMA 4 |  | NEMA 4X
4.5 A/stk | Vdc | Idc | Vpri | Ipri | 5 | Vsec l-n | Vsec l-l | 20 | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | Required |  | 100 | 200 | 100 | 200 | Model: | W | H | Depth | Surface | Required | IP33? | IP54 | IP65 |  | IP65
| (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | (CFM) |  | QTY | QTY | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU) | Fan | Fan | AC | Vortex | AC | Vortex
[37 empty] | NEMA 3R | NEMA 3R | NEMA 12 | NEMA 12
1.1111 | 600 | 5 | 380 | 6.0774 | 5 | 263 | 455.5294 | 20 | 4.98 | 4 | 30 | 7.9006 | 10 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 6.989 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.25 | 853.0355 | 40 | 55 | 20 | 35.2 | 46.816 | 4.7x4.7 | 1 | 0 | 1 | 0 | 450 | 24 | 30 | 16 | 19.3333 | 490.5355
2 | 600 | 9 | 380 | 11.0152 | 5 | 263 | 455.5294 | 20 | 8.964 | 7.25 | 30 | 14.3198 | 15 | 30 | 11.6532 | 15 | 30 | 11.7 | 15 | 15 | 12.6675 | #10 | 10 | 9.8604 | #10 | 10 | 9.9 | #10 | 0.453 | 1545.7003 | 40 | 55 | 20 | 63.7824 | 84.8306 | 4.7x4.7 | 1 | 0 | 1 | 0 | 450 | 24 | 30 | 16 | 19.3333 | 1183.2003
4 | 600 | 18 | 380 | 22.0305 | 5 | 263 | 455.5294 | 20 | 17.928 | 14.5 | 30 | 28.6396 | 30 | 30 | 23.3064 | 25 | 30 | 23.4 | 25 | 15 | 25.335 | #10 | 10 | 19.7208 | #10 | 10 | 19.8 | #10 | 0.906 | 3091.4007 | 40 | 55 | 20 | 127.5648 | 169.6612 | 6 inch | 0 | 1 | 0 | 1 | 600 | 24 | 48 | 16 | 29.3333 | 2541.4007
6 | 600 | 27 | 380 | 33.4255 | 5 | 263 | 455.5294 | 20 | 26.892 | 22 | 30 | 43.4532 | 50 | 30 | 34.9596 | 40 | 30 | 35.1 | 40 | 15 | 38.4394 | #10 | 10 | 29.5812 | #10 | 10 | 29.7 | #10 | 1.374 | 4688.2831 | 40 | 55 | 20 | 193.4592 | 257.3007 | 6 inch | 0 | 1 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 4138.2831
8 | 600 | 36 | 380 | 44.0609 | 5 | 263 | 455.5294 | 20 | 35.856 | 29 | 30 | 57.2792 | 60 | 30 | 46.6128 | 50 | 30 | 46.8 | 50 | 15 | 50.6701 | #8 | 10 | 39.4416 | #10 | 10 | 39.6 | #10 | 1.812 | 6182.8013 | 40 | 55 | 20 | 255.1296 | 339.3224 | 6 inch | 0 | 2 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 5632.8013
9.1111 | 600 | 41 | 380 | 50.1383 | 5 | 263 | 455.5294 | 20 | 40.836 | 33 | 30 | 65.1798 | 70 | 30 | 53.0868 | 60 | 30 | 53.3 | 60 | 15 | 57.6591 | #8 | 10 | 44.9196 | #8 | 10 | 45.1 | #8 | 2.062 | 7035.8368 | 40 | 55 | 20 | 290.3296 | 386.1384 | 6 inch | 0 | 2 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 6485.8368
10 | 600 | 45 | 380 | 54.6963 | 5 | 263 | 455.5294 | 20 | 44.82 | 36 | 30 | 71.1052 | 80 | 30 | 58.266 | 60 | 30 | 58.5 | 60 | 15 | 62.9008 | #6 | 10 | 49.302 | #8 | 10 | 49.5 | #8 | 2.25 | 7677.3195 | 40 | 55 | 20 | 316.8 | 421.344 | 6 inch | 0 | 2 | 0 | 4 | 600 | 24 | 48 | 16 | 29.3333 | 7127.3195
12 | 600 | 54 | 380 | 65.3317 | 5 | 263 | 455.5294 | 20 | 53.784 | 43 | 30 | 84.9313 | 90 | 30 | 69.9192 | 70 | 30 | 70.2 | 70 | 15 | 75.1315 | #6 | 10 | 59.1624 | #8 | 10 | 59.4 | #8 | 2.688 | 9171.8377 | 40 | 55 | 20 | 378.4704 | 503.3656 | 6 inch | 0 | 2 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 8272.8794
14 | 600 | 63 | 380 | 75.9671 | 5 | 263 | 455.5294 | 20 | 62.748 | 50 | 30 | 98.7573 | 100 | 30 | 81.5724 | 90 | 30 | 81.9 | 90 | 15 | 87.3622 | #4 | 10 | 69.0228 | #6 | 10 | 69.3 | #6 | 3.126 | 10666.3559 | 40 | 55 | 20 | 440.1408 | 585.3873 | 6 inch | 0 | 4 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 9767.3976
16 | 600 | 72 | 380 | 86.6025 | 5 | 263 | 455.5294 | 20 | 71.712 | 57 | 30 | 112.5833 | 125 | 30 | 93.2256 | 100 | 30 | 93.6 | 100 | 15 | 99.5929 | #4 | 10 | 78.8832 | #6 | 10 | 79.2 | #6 | 3.564 | 12160.8741 | 40 | 55 | 20 | 501.8112 | 667.4089 | 6 inch | 0 | 4 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 11261.9158
18 | 600 | 81 | 380 | 97.2379 | 5 | 263 | 455.5294 | 20 | 80.676 | 64 | 30 | 126.4093 | 150 | 30 | 104.8788 | 110 | 30 | 105.3 | 110 | 15 | 111.8236 | #3 | 10 | 88.7436 | #4 | 10 | 89.1 | #4 | 4.002 | 13655.3923 | 40 | 55 | 20 | 563.4816 | 749.4305 | 6 inch | 0 | 4 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 12756.434
24 | 600 | 108 | 380 | 129.1441 | 5 | 263 | 455.5294 | 20 | 107.568 | 85 | 30 | 167.8874 | 175 | 30 | 139.8384 | 150 | 30 | 140.4 | 150 | 15 | 148.5158 | #1 | 10 | 118.3248 | #3 | 10 | 118.8 | #3 | 5.316 | 18138.9469 | 40 | 55 | 20 | 748.4928 | 995.4954 | 6 inch | 0 | 4 | 0 | 6 | 800 | 34 | 48 | 28 | 47.9444 | 17239.9885
30 | 600 | 135 | 380 | 162.5697 | 5 | 263 | 455.5294 | 20 | 134.46 | 107 | 30 | 211.3406 | 225 | 30 | 174.798 | 175 | 30 | 175.5 | 175 | 15 | 186.9551 | #1/0 | 10 | 147.906 | #1 | 10 | 148.5 | #1 | 6.69 | 22827.23 | 40 | 55 | 20 | 941.952 | 1252.7962 | 6 inch | 0 | 6 | 0 | 8 | 800 | 34 | 48 | 28 | 47.9444 | 21928.2716
32 | 600 | 144 | 380 | 173.2051 | 5 | 263 | 455.5294 | 20 | 143.424 | 114 | 30 | 225.1666 | 225 | 30 | 186.4512 | 200 | 30 | 187.2 | 200 | 15 | 199.1858 | #2/0 | 10 | 157.7664 | #1 | 10 | 158.4 | #1 | 7.128 | 24321.7482 | 40 | 55 | 20 | 1003.6224 | 1334.8178 | 6 inch | 0 | 6 | 0 | 8 | 800 | 34 | 48 | 28 | 47.9444 | 23422.7898
40 | 600 | 180 | 380 | 215.7467 | 5 | 263 | 455.5294 | 20 | 179.28 | 142 | 30 | 280.4707 | 300 | 30 | 233.064 | 250 | 30 | 234 | 250 | 15 | 248.1087 | #3/0 | 10 | 197.208 | #2/0 | 10 | 198 | #2/0 | 8.88 | 30299.821 | 40 | 55 | 20 | 1250.304 | 1662.9043 | 6 inch | 0 | 8 | 0 | 10 | 1250 | 38 | 70 | 28 | 71.5556 | 28958.1543
48 | 600 | 216 | 380 | 258.2883 | 5 | 263 | 455.5294 | 20 | 215.136 | 170 | 30 | 335.7748 | 350 | 30 | 279.6768 | 300 | 30 | 280.8 | 300 | 15 | 297.0315 | #4/0 | 10 | 236.6496 | #3/0 | 10 | 237.6 | #3/0 | 10.632 | 36277.8937 | 40 | 55 | 20 | 1496.9856 | 1990.9908 | 6 inch | 0 | 8 | 0 | 10 | 1250 | 38 | 70 | 28 | 71.5556 | 34936.2271
| Specs: |  |  |  |  | Transformer Sizing (3 Phase) |  |  |  | (Iac): Circuit Breaker Sizing; Scale: Wire Sizing | [7 empty] | Heat Dissipation |  | Environment |  | Fan Sizing | [7 empty] | Air Conditionner Sizing | [5 empty] | Enclosure Type
# Stacks | Output |  | Input |  |  | k6 rated-115deg C-50/60 Hz |  |  |  | (Iac): Primary Input; Prim: Secondary Output; (Idc): DC Output; Scale: Primary |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  | NEMA 3R | NEMA 12 | Fan Type | Fan CFM | Fan CFM | Fan CFM | Fan CFM | Encl.Size | [5 empty] | NEMA 3R | NEMA 12 | NEMA 4 |  | NEMA 4X
4.5 A/stk | Vdc | Idc | Vpri | Ipri | 5 | Vsec l-n | Vsec l-l | 20 | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | Required |  | 100 | 200 | 100 | 200 | Model: | W | H | Depth | Surface | Required | IP33? | IP54 | IP65 |  | IP65
| (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | (CFM) |  | QTY | QTY | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU) | Fan | Fan+ Filter | AC | Vortex | AC | Vortex
[37 empty] | NEMA 3R | NEMA 3R | NEMA 12 | NEMA 12
1.1111 | 400 | 5 | 380 | 4.1782 | 5 | 179.76 | 311.3535 | 20 | 4.98 | 2.75 | 30 | 5.4317 | 10 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 4.8049 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.175 | 597.1248 | 40 | 55 | 20 | 24.64 | 32.7712 | 4.7x4.7 | 1 | 0 | 1 | 0 | 450 | 24 | 30 | 16 | 19.3333 | 234.6248
2 | 400 | 9 | 380 | 7.5967 | 5 | 179.76 | 311.3535 | 20 | 8.964 | 5 | 30 | 9.8757 | 10 | 30 | 11.6532 | 15 | 30 | 11.7 | 15 | 15 | 8.7362 | #10 | 10 | 9.8604 | #10 | 10 | 9.9 | #10 | 0.318 | 1085.0612 | 40 | 55 | 20 | 44.7744 | 59.55 | 4.7x4.7 | 1 | 0 | 1 | 0 | 450 | 24 | 30 | 16 | 19.3333 | 722.5612
4 | 400 | 18 | 380 | 14.8136 | 5 | 179.76 | 311.3535 | 20 | 17.928 | 9.75 | 30 | 19.2577 | 20 | 30 | 23.3064 | 25 | 30 | 23.4 | 25 | 15 | 17.0356 | #10 | 10 | 19.7208 | #10 | 10 | 19.8 | #10 | 0.621 | 2118.9402 | 40 | 55 | 20 | 87.4368 | 116.2909 | 6 inch | 0 | 1 | 0 | 1 | 600 | 24 | 48 | 16 | 29.3333 | 1568.9402
6 | 400 | 27 | 380 | 22.7901 | 5 | 179.76 | 311.3535 | 20 | 26.892 | 15 | 30 | 29.6272 | 30 | 30 | 34.9596 | 40 | 30 | 35.1 | 40 | 15 | 26.2087 | #10 | 10 | 29.5812 | #10 | 10 | 29.7 | #10 | 0.954 | 3255.1835 | 40 | 55 | 20 | 134.3232 | 178.6499 | 6 inch | 0 | 1 | 0 | 1 | 600 | 24 | 48 | 16 | 29.3333 | 2705.1835
8 | 400 | 36 | 380 | 29.6272 | 5 | 179.76 | 311.3535 | 20 | 35.856 | 19.5 | 30 | 38.5153 | 40 | 30 | 46.6128 | 50 | 30 | 46.8 | 50 | 15 | 34.0713 | #10 | 10 | 39.4416 | #10 | 10 | 39.6 | #10 | 1.242 | 4237.8804 | 40 | 55 | 20 | 174.8736 | 232.5819 | 6 inch | 0 | 1 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 3687.8804
9.1111 | 400 | 41 | 380 | 34.9449 | 5 | 179.76 | 311.3535 | 20 | 40.836 | 23 | 30 | 45.4284 | 50 | 30 | 53.0868 | 60 | 30 | 53.3 | 60 | 15 | 40.1866 | #8 | 10 | 44.9196 | #8 | 10 | 45.1 | #8 | 1.462 | 4988.5516 | 40 | 55 | 20 | 205.8496 | 273.78 | 6 inch | 0 | 2 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 4438.5516
10 | 400 | 45 | 380 | 37.9836 | 5 | 179.76 | 311.3535 | 20 | 44.82 | 25 | 30 | 49.3786 | 50 | 30 | 58.266 | 60 | 30 | 58.5 | 60 | 15 | 43.6811 | #8 | 10 | 49.302 | #8 | 10 | 49.5 | #8 | 1.59 | 5425.3058 | 40 | 55 | 20 | 223.872 | 297.7498 | 6 inch | 0 | 2 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 4875.3058
12 | 400 | 54 | 380 | 45.5803 | 5 | 179.76 | 311.3535 | 20 | 53.784 | 30 | 30 | 59.2544 | 60 | 30 | 69.9192 | 70 | 30 | 70.2 | 70 | 15 | 52.4173 | #8 | 10 | 59.1624 | #8 | 10 | 59.4 | #8 | 1.908 | 6510.3669 | 40 | 55 | 20 | 268.6464 | 357.2997 | 6 inch | 0 | 2 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 5960.3669
14 | 400 | 63 | 380 | 51.6577 | 5 | 179.76 | 311.3535 | 20 | 62.748 | 34 | 30 | 67.155 | 70 | 30 | 81.5724 | 90 | 30 | 81.9 | 90 | 15 | 59.4063 | #8 | 10 | 69.0228 | #6 | 10 | 69.3 | #6 | 2.166 | 7390.6996 | 40 | 55 | 20 | 304.9728 | 405.6138 | 6 inch | 0 | 2 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 6491.7412
16 | 400 | 72 | 380 | 59.2544 | 5 | 179.76 | 311.3535 | 20 | 71.712 | 39 | 30 | 77.0307 | 80 | 30 | 93.2256 | 100 | 30 | 93.6 | 100 | 15 | 68.1425 | #6 | 10 | 78.8832 | #6 | 10 | 79.2 | #6 | 2.484 | 8475.7607 | 40 | 55 | 20 | 349.7472 | 465.1638 | 6 inch | 0 | 2 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 7576.8024
18 | 400 | 81 | 380 | 66.8511 | 5 | 179.76 | 311.3535 | 20 | 80.676 | 44 | 30 | 86.9064 | 90 | 30 | 104.8788 | 110 | 30 | 105.3 | 110 | 15 | 76.8787 | #6 | 10 | 88.7436 | #4 | 10 | 89.1 | #4 | 2.802 | 9560.8219 | 40 | 55 | 20 | 394.5216 | 524.7137 | 6 inch | 0 | 2 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 8661.8636
24 | 400 | 108 | 380 | 89.6412 | 5 | 179.76 | 311.3535 | 20 | 107.568 | 59 | 30 | 116.5336 | 125 | 30 | 139.8384 | 150 | 30 | 140.4 | 150 | 15 | 103.0874 | #4 | 10 | 118.3248 | #3 | 10 | 118.8 | #3 | 3.756 | 12816.0054 | 40 | 55 | 20 | 528.8448 | 703.3636 | 6 inch | 0 | 4 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 11917.047
30 | 400 | 135 | 380 | 110.912 | 5 | 179.76 | 311.3535 | 20 | 134.46 | 73 | 30 | 144.1856 | 150 | 30 | 174.798 | 175 | 30 | 175.5 | 175 | 15 | 127.5488 | #2 | 10 | 147.906 | #1 | 10 | 148.5 | #1 | 4.65 | 15866.4603 | 40 | 55 | 20 | 654.72 | 870.7776 | 6 inch | 0 | 4 | 0 | 6 | 800 | 34 | 48 | 28 | 47.9444 | 14967.502
32 | 400 | 144 | 380 | 118.5087 | 5 | 179.76 | 311.3535 | 20 | 143.424 | 78 | 30 | 154.0614 | 175 | 30 | 186.4512 | 200 | 30 | 187.2 | 200 | 15 | 136.2851 | #2 | 10 | 157.7664 | #1 | 10 | 158.4 | #1 | 4.968 | 16951.5215 | 40 | 55 | 20 | 699.4944 | 930.3276 | 6 inch | 0 | 4 | 0 | 6 | 800 | 34 | 48 | 28 | 47.9444 | 16052.5631
40 | 400 | 180 | 380 | 147.3763 | 5 | 179.76 | 311.3535 | 20 | 179.28 | 97 | 30 | 191.5891 | 200 | 30 | 233.064 | 250 | 30 | 234 | 250 | 15 | 169.4827 | #1/0 | 10 | 197.208 | #2/0 | 10 | 198 | #2/0 | 6.18 | 21087.0376 | 40 | 55 | 20 | 870.144 | 1157.2915 | 6 inch | 0 | 6 | 0 | 6 | 1250 | 38 | 70 | 28 | 71.5556 | 19745.3709
222.2222 | 100 | 1000 | 380 | 205.1113 | 5 | 44.94 | 77.8384 | 20 | 996 | 135 | 30 | 266.6447 | 300 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 235.878 | #3/0 | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 10.1 | 34462.6342 | 40 | 55 | 20 | 1422.08 | 1891.3664 | 6 inch | 0 | 8 | 0 | 10 | 1250 | 38 | 70 | 28 | 71.5556 | 33120.9675
Wire Sizing is based on the nominal current x SF
| Specs: |  |  |  |  | Transformer Sizing (3 Phase) |  |  |  | (Iac): Circuit Breaker Sizing; Scale: Wire Sizing | [7 empty] | Heat Dissipation |  | Environment |  | Fan Sizing | [7 empty] | Air Conditionner Sizing | [5 empty] | Enclosure Type
# Stacks | Output |  | Input |  |  | k6 rated-115deg C-50/60 Hz |  |  |  | (Iac): Primary Input; Prim: Secondary Output; (Idc): DC Output; Scale: Primary |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  | NEMA 3R | NEMA 12 | Fan Type | Fan CFM | Fan CFM | Fan CFM | Fan CFM | Encl.Size |  | H+3" for feet |  |  |  | NEMA 3R | NEMA 12 | NEMA 4 |  | NEMA 4X
5.2 A/stk | Vdc | Idc | Vpri | Ipri | 5 | Vsec l-n | Vsec l-l | 20 | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 60 | 10 | Required | Required |  | 100 | 200 | 100 | 200 | Model: | W | H | Depth | Surface | Required | IP33? | IP54 | IP65 |  | IP65
| (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | (CFM) |  | QTY | QTY | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU) | Fan | Fan+ Filter | AC | Vortex | AC | Vortex
[37 empty] | NEMA 3R | NEMA 3R | NEMA 12 | NEMA 12
1 | 300 | 5.2 | 380 | 3.4185 | 5 | 134.82 | 233.5151 | 20 | 5.1792 | 2.25 | 30 | 4.4441 | 15 | 30 | 6.733 | 10 | 30 | 6.76 | 10 | 15 | 3.9313 | #10 | 10 | 5.6971 | #10 | 10 | 5.72 | #10 | 0.1454 | 496.1254 | 40 | 60 | 10 | 14.0747 | 18.7194 | 4.7x4.7 | 1 | 0 | 1 | 0 | 450 | 24 | 30 | 16 | 19.3333 | 12.7921
3 | 300 | 15.6 | 380 | 9.8757 | 5 | 134.82 | 233.5151 | 20 | 15.5376 | 6.5 | 30 | 12.8384 | 15 | 30 | 20.1989 | 25 | 30 | 20.28 | 25 | 15 | 11.3571 | #10 | 10 | 17.0914 | #10 | 10 | 17.16 | #10 | 0.4212 | 1437.1942 | 40 | 60 | 10 | 40.7722 | 54.227 | 6 inch | 0 | 1 | 0 | 1 | 600 | 24 | 48 | 16 | 29.3333 | 703.8609
6 | 300 | 31.2 | 380 | 19.7515 | 5 | 134.82 | 233.5151 | 20 | 31.0752 | 13 | 30 | 25.6769 | 30 | 30 | 40.3978 | 50 | 30 | 40.56 | 50 | 15 | 22.7142 | #10 | 10 | 34.1827 | #10 | 10 | 34.32 | #10 | 0.8424 | 2874.3884 | 40 | 60 | 10 | 81.5443 | 108.4539 | 6 inch | 0 | 1 | 0 | 1 | 600 | 24 | 48 | 16 | 29.3333 | 2141.0551
9 | 300 | 46.8 | 380 | 28.8675 | 5 | 134.82 | 233.5151 | 20 | 46.6128 | 19 | 30 | 37.5278 | 40 | 30 | 60.5966 | 60 | 30 | 60.84 | 60 | 15 | 33.1976 | #10 | 10 | 51.2741 | #8 | 10 | 51.48 | #8 | 1.2336 | 4209.2184 | 40 | 60 | 10 | 119.4125 | 158.8186 | 6 inch | 0 | 1 | 0 | 1 | 600 | 24 | 48 | 16 | 29.3333 | 3475.885
12 | 300 | 62.4 | 380 | 39.5029 | 5 | 134.82 | 233.5151 | 20 | 62.1504 | 26 | 30 | 51.3538 | 60 | 30 | 80.7955 | 90 | 30 | 81.12 | 90 | 15 | 45.4284 | #8 | 10 | 68.3654 | #6 | 10 | 68.64 | #6 | 1.6848 | 5748.7768 | 40 | 60 | 10 | 163.0886 | 216.9079 | 6 inch | 0 | 1 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 5015.4435
15 | 300 | 78 | 380 | 48.619 | 5 | 134.82 | 233.5151 | 20 | 77.688 | 32 | 30 | 63.2047 | 70 | 30 | 100.9944 | 110 | 30 | 101.4 | 110 | 15 | 55.9118 | #8 | 10 | 85.4568 | #4 | 10 | 85.8 | #4 | 2.076 | 7083.6068 | 40 | 60 | 10 | 200.9568 | 267.2725 | 6 inch | 0 | 2 | 0 | 2 | 600 | 24 | 48 | 16 | 29.3333 | 6350.2735
18 | 300 | 93.6 | 380 | 57.735 | 5 | 134.82 | 233.5151 | 20 | 93.2256 | 38 | 30 | 75.0555 | 80 | 30 | 121.1933 | 125 | 30 | 121.68 | 125 | 15 | 66.3953 | #6 | 10 | 102.5482 | #4 | 10 | 102.96 | #4 | 2.4672 | 8418.4367 | 40 | 60 | 10 | 238.825 | 317.6372 | 6 inch | 0 | 2 | 0 | 2 | 800 | 24 | 48 | 28 | 39.3333 | 7435.1034
24 | 300 | 124.8 | 380 | 77.4865 | 5 | 134.82 | 233.5151 | 20 | 124.3008 | 51 | 30 | 100.7324 | 125 | 30 | 161.591 | 175 | 30 | 162.24 | 175 | 15 | 89.1095 | #4 | 10 | 136.7309 | #2 | 10 | 137.28 | #2 | 3.3096 | 11292.8252 | 40 | 60 | 10 | 320.3693 | 426.0911 | 6 inch | 0 | 2 | 0 | 4 | 800 | 24 | 48 | 28 | 39.3333 | 10309.4918
27 | 300 | 140.4 | 380 | 86.6025 | 5 | 134.82 | 233.5151 | 20 | 139.8384 | 57 | 30 | 112.5833 | 125 | 30 | 181.7899 | 200 | 30 | 182.52 | 200 | 15 | 99.5929 | #4 | 10 | 153.8222 | #1 | 10 | 154.44 | #1 | 3.7008 | 12627.6551 | 40 | 60 | 10 | 358.2374 | 476.4558 | 6 inch | 0 | 2 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 11429.044
30 | 300 | 156 | 380 | 95.7186 | 5 | 134.82 | 233.5151 | 20 | 155.376 | 63 | 30 | 124.4342 | 125 | 30 | 201.9888 | 225 | 30 | 202.8 | 225 | 15 | 110.0764 | #3 | 10 | 170.9136 | #1/0 | 10 | 171.6 | #1/0 | 4.092 | 13962.4851 | 40 | 60 | 10 | 396.1056 | 526.8204 | 6 inch | 0 | 2 | 0 | 4 | 800 | 34 | 48 | 28 | 47.9444 | 12763.874
[26 empty] | Required | Cooling
Manufact | Model | BTU | Kw | NEMA | size | Mounting | [18 empty] | (kW) | (BTU) | (BTU) | reqd
Kooltronic | 1RP | 1000 | 0.29307 | 12 | 17.5x12.5x11 | SIDE | [21 empty] | (kW)
Hammond | DTS1200 | 1200 | 0.35169 | 12 |  | SIDE
Vortec |  | 1600 | 0.46891 | 4X |  | SIDE | [18 empty] | 0.205 | 699.4891 | 336.9891 | 0.098762 | 0.10624
Vortec |  | 1800 | 0.52753 | 12 |  | SIDE | [18 empty] | 0.348 | 1187.4254 | 824.9254 | 0.24176 | 0.10624
Kooltronic |  | 2000 | 0.58614 | 12 | 17.5x12.5x11 | SIDE | [18 empty] | 0.696 | 2374.8508 | 1824.8508 | 0.53481 | 0.16119
Kooltronic |  | 2000 | 0.58614 | 12 | 28x12.5x11 | SIDE
Kooltronic |  | 2000 | 0.58614 | 12 |  | SIDE
Kooltronic |  |  | 0 | [21 empty] | 1.044 | 3562.2762 | 3012.2762 | 0.88281 | 0.16119
Hammond | DTS2000 | 2000 | 0.58614 | 12 |  | SIDE | [18 empty] | 1.392 | 4749.7017 | 4199.7017 | 1.2308 | 0.16119
Hammond | DTS2000SS | 2000 | 0.58614 | 4X |  | SIDE | [18 empty] | 1.582 | 5398.0086 | 4848.0086 | 1.4208 | 0.16119
Vortec |  | 2200 | 0.64476 | 12 |  | TOP | [18 empty] | 1.77 | 6039.4913 | 5489.4913 | 1.6088 | 0.16119
Vortec |  | 2200 | 0.64476 | 4X |  | SIDE | [18 empty] | 2.088 | 7124.5525 | 6574.5525 | 1.9268 | 0.16119
Hammond | DTS3500 | 3500 | 1.0257 | 12 |  | side | [18 empty] | 2.466 | 8414.3422 | 7515.3838 | 2.2025 | 0.26346
Vortec |  | 4000 | 1.1723 | 12 |  | SIDE | [18 empty] | 2.784 | 9499.4033 | 8600.445 | 2.5205 | 0.26346
Vortec |  | 4000 | 1.1723 | 4X |  | SIDE | [18 empty] | 3.102 | 10584.4645 | 9685.5062 | 2.8385 | 0.26346
Hammond | DTS4500 | 4500 | 1.3188 | 12 |  | TOP | [18 empty] | 4.176 | 14249.105 | 13350.1467 | 3.9125 | 0.26346
Vortec |  | 6000 | 1.7584 | 12 |  | SIDE | [18 empty] | 5.19 | 17709.017 | 16810.0586 | 4.9265 | 0.26346
Hammond | DTS6000 | 6000 | 1.7584 | 12 |  | SIDE | [18 empty] | 5.568 | 18998.8067 | 18099.8483 | 5.3045 | 0.26346
Hammond | DTS8000 | 8000 | 2.3446 | 12 |  | SIDE | [18 empty] | 6.9 | 23543.7798 | 22202.1131 | 6.5068 | 0.3932
Vortec |  | 8500 | 2.4911 | 4X |  | SIDE | [18 empty] | 8.292 | 28293.4815 | 26951.8148 | 7.8988 | 0.3932
Hammond | DTS12000 | 12000 | 3.5169 | 12 |  | SIDE

## 1PH Battery Chargers
1 PHASE Battery Chargers | [6 empty] | VERIFIER LES COEFFICIENT DES TRANSFOS AVEC DES MODELES EXISTANTS
Vnom | Idc | #cel | VPC | Vmax | Vsec | Isec | Psec | P | Iprim | At Vac | CB1 | AWG | AWG | AWG | CB2 | SCR | VM | AM | fuse | TVS | ALARM
(Vdc) | (Idc) |  | (Vdc) | (Vdc) | (Vac) | (Iac) | (Kva) | (Kva) | (Iac) | (Vac) | (Iac) | Prim | Sec | DC | (Idc) | Model | Scale | Scale | (A) |  | 5 RELAY
Specs: | [6 empty] | Transformer Sizing (1 Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size |  |  |  |  | AC
120 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
60 | 2.45 | 147 | 5 | 240 | 6.25 | 12 | 182.7504 | 35 | 7.4925 | 1.5 | 35 | 8.4375 | 10 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 7.1875 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.085 | 290.0321 | 40 | 55 | 20 | 11.968 | 0.13298 | 0.066489 | 450 | 24 | 30 | 16 | 19.3333 | -72.4679
92 | 1.7 | 156.4 | 10 | 120 | 25 | 12 | 194.4365 | 35 | 14.985 | 3 | 35 | 33.75 | 40 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 28.75 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.17 | 580.0641 | 40 | 55 | 20 | 23.936 | 0.26596 | 0.13298 | 450 | 24 | 30 | 16 | 19.3333 | 217.5641
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
12 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
6 | 2.45 | 14.7 | 5 | 120 | 2.0833 | 12 | 20.275 | 35 | 7.4925 | 0.25 | 35 | 2.8125 | 5 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 2.3958 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.0225 | 76.7732 | 40 | 55 | 20 | 3.168 | 0.0352 | 0.0176 | 450 | 24 | 30 | 16 | 19.3333 | -285.7268
6 | 2.45 | 14.7 | 10 | 120 | 4.1667 | 12 | 20.275 | 35 | 14.985 | 0.5 | 35 | 5.625 | 10 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 4.7917 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.045 | 153.5464 | 40 | 55 | 20 | 6.336 | 0.0704 | 0.0352 | 450 | 24 | 30 | 16 | 19.3333 | -208.9536
6 | 2.45 | 14.7 | 15 | 120 | 4.1667 | 12 | 20.275 | 35 | 22.4775 | 0.5 | 35 | 5.625 | 10 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 4.7917 | #10 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.055 | 187.6678 | 40 | 55 | 20 | 7.744 | 0.086044 | 0.043022 | 450 | 24 | 30 | 16 | 19.3333 | -174.8322
6 | 2.45 | 14.7 | 20 | 120 | 6.25 | 12 | 20.275 | 35 | 29.97 | 0.75 | 35 | 8.4375 | 10 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 7.1875 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.0775 | 264.441 | 40 | 55 | 20 | 10.912 | 0.12124 | 0.060622 | 450 | 24 | 30 | 16 | 19.3333 | -98.059
6 | 2.45 | 14.7 | 25 | 120 | 8.3333 | 12 | 20.275 | 35 | 37.4625 | 1 | 35 | 11.25 | 15 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 9.5833 | #10 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.1 | 341.2142 | 40 | 55 | 20 | 14.08 | 0.15644 | 0.078222 | 450 | 24 | 30 | 16 | 19.3333 | -21.2858
6 | 2.45 | 14.7 | 30 | 120 | 8.3333 | 12 | 20.275 | 35 | 44.955 | 1 | 35 | 11.25 | 15 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 9.5833 | #10 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.11 | 375.3356 | 40 | 55 | 20 | 15.488 | 0.17209 | 0.086044 | 450 | 24 | 30 | 16 | 19.3333 | 12.8356
6 | 2.45 | 14.7 | 35 | 120 | 10.4167 | 12 | 20.275 | 35 | 52.4475 | 1.25 | 35 | 14.0625 | 15 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 11.9792 | #10 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 0.1325 | 452.1088 | 40 | 55 | 20 | 18.656 | 0.20729 | 0.10364 | 450 | 24 | 30 | 16 | 19.3333 | 89.6088
6 | 2.45 | 14.7 | 40 | 120 | 10.4167 | 12 | 20.275 | 35 | 59.94 | 1.25 | 35 | 14.0625 | 15 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 11.9792 | #10 | 10 | 65.934 | #6 | 10 | 44 | #8 | 0.1425 | 486.2302 | 40 | 55 | 20 | 20.064 | 0.22293 | 0.11147 | 450 | 24 | 30 | 16 | 19.3333 | 123.7302
6 | 2.45 | 14.7 | 50 | 120 | 14.5833 | 12 | 20.275 | 35 | 74.925 | 1.75 | 35 | 19.6875 | 20 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 16.7708 | #10 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 0.1875 | 639.7766 | 40 | 55 | 20 | 26.4 | 0.29333 | 0.14667 | 450 | 24 | 30 | 16 | 19.3333 | 277.2766
6 | 2.45 | 14.7 | 60 | 120 | 16.6667 | 12 | 20.275 | 35 | 89.91 | 2 | 35 | 22.5 | 25 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 19.1667 | #10 | 10 | 98.901 | #4 | 10 | 66 | #6 | 0.22 | 750.6712 | 40 | 55 | 20 | 30.976 | 0.34418 | 0.17209 | 450 | 24 | 30 | 16 | 19.3333 | 388.1712
6 | 2.45 | 14.7 | 75 | 120 | 20.8333 | 12 | 20.275 | 35 | 112.3875 | 2.5 | 35 | 28.125 | 30 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 23.9583 | #10 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 0.275 | 938.3391 | 40 | 55 | 20 | 38.72 | 0.43022 | 0.21511 | 450 | 24 | 30 | 16 | 19.3333 | 575.8391
6 | 2.45 | 14.7 | 100 | 120 | 27.0833 | 12 | 20.275 | 35 | 149.85 | 3.25 | 35 | 36.5625 | 40 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 31.1458 | #10 | 10 | 164.835 | #1 | 10 | 110 | #3 | 0.3625 | 1236.9015 | 40 | 55 | 20 | 51.04 | 0.56711 | 0.28356 | 450 | 24 | 30 | 16 | 19.3333 | 874.4015
6 | 2.45 | 14.7 | 125 | 120 | 33.3333 | 12 | 20.275 | 35 | 187.3125 | 4 | 35 | 45 | 50 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 38.3333 | #10 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 0.45 | 1535.4639 | 40 | 55 | 20 | 63.36 | 0.704 | 0.352 | 450 | 24 | 30 | 16 | 19.3333 | 1172.9639
6 | 2.45 | 14.7 | 150 | 120 | 39.5833 | 12 | 20.275 | 35 | 224.775 | 4.75 | 35 | 53.4375 | 60 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 45.5208 | #8 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 0.5375 | 1834.0263 | 40 | 55 | 20 | 75.68 | 0.84089 | 0.42044 | 450 | 24 | 30 | 16 | 19.3333 | 1471.5263
6 | 2.45 | 14.7 | 175 | 208 | 26.4423 | 12 | 20.275 | 35 | 262.2375 | 5.5 | 35 | 35.6971 | 40 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 30.4087 | #10 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 0.625 | 2132.5887 | 40 | 55 | 20 | 88 | 0.97778 | 0.48889 | 450 | 24 | 30 | 16 | 19.3333 | 1770.0887
6 | 2.45 | 14.7 | 200 | 208 | 30.0481 | 12 | 20.275 | 35 | 299.7 | 6.25 | 35 | 40.5649 | 50 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 34.5553 | #10 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 0.7125 | 2431.1512 | 40 | 55 | 20 | 100.32 | 1.1147 | 0.55733 | 450 | 24 | 30 | 16 | 19.3333 | 2068.6512
6 | 2.45 | 14.7 | 250 | 208 | 37.2596 | 12 | 20.275 | 35 | 374.625 | 7.75 | 35 | 50.3005 | 60 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 42.8486 | #8 | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 0.8875 | 3028.276 | 40 | 55 | 20 | 124.96 | 1.3884 | 0.69422 | 450 | 24 | 30 | 16 | 19.3333 | 2665.776
6 | 2.45 | 14.7 | 300 | 240 | 38.5417 | 12 | 20.275 | 35 | 449.55 | 9.25 | 35 | 52.0312 | 60 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 44.3229 | #8 | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 1.0625 | 3625.4009 | 40 | 55 | 20 | 149.6 | 1.6622 | 0.83111 | 450 | 24 | 30 | 16 | 19.3333 | 3262.9009
6 | 2.45 | 14.7 | 350 | 480 | 22.9167 | 12 | 20.275 | 35 | 524.475 | 11 | 35 | 30.9375 | 40 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 26.3542 | #10 | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 1.25 | 4265.1775 | 40 | 55 | 20 | 176 | 1.9556 | 0.97778 | 450 | 24 | 30 | 16 | 19.3333 | 3902.6775
6 | 2.45 | 14.7 | 400 | 480 | 26.0417 | 12 | 20.275 | 35 | 599.4 | 12.5 | 35 | 35.1563 | 40 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 29.9479 | #10 | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 1.425 | 4862.3023 | 40 | 55 | 20 | 200.64 | 2.2293 | 1.1147 | 450 | 24 | 30 | 16 | 19.3333 | 4499.8023
6 | 2.45 | 14.7 | 450 | 480 | 29.1667 | 12 | 20.275 | 35 | 674.325 | 14 | 35 | 39.375 | 40 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 33.5417 | #10 | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 1.6 | 5459.4272 | 40 | 55 | 20 | 225.28 | 2.5031 | 1.2516 | 450 | 24 | 30 | 16 | 19.3333 | 5096.9272
6 | 2.45 | 14.7 | 500 | 480 | 32.2917 | 12 | 20.275 | 35 | 749.25 | 15.5 | 35 | 43.5938 | 50 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 37.1354 | #10 | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 1.775 | 6056.552 | 40 | 55 | 20 | 249.92 | 2.7769 | 1.3884 | 450 | 24 | 30 | 16 | 19.3333 | 5694.052
6 | 2.45 | 14.7 | 600 | 480 | 38.5417 | 12 | 20.275 | 35 | 899.1 | 18.5 | 35 | 52.0312 | 60 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 44.3229 | #8 | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 2.125 | 7250.8017 | 40 | 55 | 20 | 299.2 | 3.3244 | 1.6622 | 450 | 24 | 30 | 16 | 19.3333 | 6888.3017
6 | 2.45 | 14.7 | 700 | 480 | 45.8333 | 12 | 20.275 | 35 | 1048.95 | 22 | 35 | 61.875 | 60 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 52.7083 | #8 | 10 | 1153.845 | Buss | 10 | 770 | Buss | 2.5 | 8530.355 | 40 | 55 | 20 | 352 | 3.9111 | 1.9556 | 450 | 24 | 30 | 16 | 19.3333 | 8167.855
6 | 2.45 | 14.7 | 800 | 480 | 52.0833 | 12 | 20.275 | 35 | 1198.8 | 25 | 35 | 70.3125 | 80 | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 59.8958 | #8 | 10 | 1318.68 | Buss | 10 | 880 | Buss | 2.85 | 9724.6047 | 40 | 55 | 20 | 401.28 | 4.4587 | 2.2293 | 450 | 24 | 30 | 16 | 19.3333 | 9362.1047
6 | 2.45 | 14.7 | 900 | 480 | 58.3333 | 12 | 20.275 | 35 | 1348.65 | 28 | 35 | 78.75 | 80 | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 67.0833 | #6 | 10 | 1483.515 | Buss | 10 | 990 | Buss | 3.2 | 10918.8544 | 40 | 55 | 20 | 450.56 | 5.0062 | 2.5031 | 450 | 24 | 30 | 16 | 19.3333 | 10556.3544
6 | 2.45 | 14.7 | 1000 | 480 | 64.5833 | 12 | 20.275 | 35 | 1498.5 | 31 | 35 | 87.1875 | 90 | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 74.2708 | #6 | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 3.55 | 12113.1041 | 40 | 55 | 20 | 499.84 | 5.5538 | 2.7769 | 450 | 24 | 30 | 16 | 19.3333 | 11750.6041
6 | 2.45 | 14.7 | 1100 | 480 | 70.8333 | 12 | 20.275 | 35 | 1648.35 | 34 | 35 | 95.625 | 100 | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 81.4583 | #4 | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 3.9 | 13307.3538 | 40 | 55 | 20 | 549.12 | 6.1013 | 3.0507 | 450 | 24 | 30 | 16 | 19.3333 | 12944.8538
6 | 2.45 | 14.7 | 1200 | 480 | 77.0833 | 12 | 20.275 | 35 | 1798.2 | 37 | 35 | 104.0625 | 110 | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 88.6458 | #4 | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 4.25 | 14501.6035 | 40 | 55 | 20 | 598.4 | 6.6489 | 3.3244 | 450 | 24 | 30 | 16 | 19.3333 | 14139.1035
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
24 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
12 | 2.45 | 29.4 | 5 | 120 | 4.1667 | 12 | 38.5501 | 35 | 7.4925 | 0.5 | 35 | 5.625 | 10 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 4.7917 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.035 | 119.425 | 40 | 55 | 20 | 4.928 | 0.054756 | 0.027378 | 450 | 24 | 30 | 16 | 19.3333 | -243.075
12 | 2.45 | 29.4 | 10 | 120 | 6.25 | 12 | 38.5501 | 35 | 14.985 | 0.75 | 35 | 8.4375 | 10 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 7.1875 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.0575 | 196.1982 | 40 | 55 | 20 | 8.096 | 0.089956 | 0.044978 | 450 | 24 | 30 | 16 | 19.3333 | -166.3018
12 | 2.45 | 29.4 | 15 | 120 | 8.3333 | 12 | 38.5501 | 35 | 22.4775 | 1 | 35 | 11.25 | 15 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 9.5833 | #10 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.08 | 272.9714 | 40 | 55 | 20 | 11.264 | 0.12516 | 0.062578 | 450 | 24 | 30 | 16 | 19.3333 | -89.5286
12 | 2.45 | 29.4 | 20 | 120 | 10.4167 | 12 | 38.5501 | 35 | 29.97 | 1.25 | 35 | 14.0625 | 15 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 11.9792 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.1025 | 349.7446 | 40 | 55 | 20 | 14.432 | 0.16036 | 0.080178 | 450 | 24 | 30 | 16 | 19.3333 | -12.7554
12 | 2.45 | 29.4 | 25 | 120 | 12.5 | 12 | 38.5501 | 35 | 37.4625 | 1.5 | 35 | 16.875 | 20 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 14.375 | #10 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.125 | 426.5178 | 40 | 55 | 20 | 17.6 | 0.19556 | 0.097778 | 450 | 24 | 30 | 16 | 19.3333 | 64.0178
12 | 2.45 | 29.4 | 30 | 120 | 14.5833 | 12 | 38.5501 | 35 | 44.955 | 1.75 | 35 | 19.6875 | 20 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 16.7708 | #10 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.1475 | 503.2909 | 40 | 55 | 20 | 20.768 | 0.23076 | 0.11538 | 450 | 24 | 30 | 16 | 19.3333 | 140.7909
12 | 2.45 | 29.4 | 35 | 120 | 18.75 | 12 | 38.5501 | 35 | 52.4475 | 2.25 | 35 | 25.3125 | 30 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 21.5625 | #10 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 0.1825 | 622.7159 | 40 | 55 | 20 | 25.696 | 0.28551 | 0.14276 | 450 | 24 | 30 | 16 | 19.3333 | 260.2159
12 | 2.45 | 29.4 | 40 | 120 | 20.8333 | 12 | 38.5501 | 35 | 59.94 | 2.5 | 35 | 28.125 | 30 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 23.9583 | #10 | 10 | 65.934 | #6 | 10 | 44 | #8 | 0.205 | 699.4891 | 40 | 55 | 20 | 28.864 | 0.32071 | 0.16036 | 450 | 24 | 30 | 16 | 19.3333 | 336.9891
12 | 2.45 | 29.4 | 50 | 120 | 25 | 12 | 38.5501 | 35 | 74.925 | 3 | 35 | 33.75 | 40 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 28.75 | #10 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 0.25 | 853.0355 | 40 | 55 | 20 | 35.2 | 0.39111 | 0.19556 | 450 | 24 | 30 | 16 | 19.3333 | 490.5355
12 | 2.45 | 29.4 | 60 | 120 | 29.1667 | 12 | 38.5501 | 35 | 89.91 | 3.5 | 35 | 39.375 | 40 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 33.5417 | #10 | 10 | 98.901 | #4 | 10 | 66 | #6 | 0.295 | 1006.5819 | 40 | 55 | 20 | 41.536 | 0.46151 | 0.23076 | 450 | 24 | 30 | 16 | 19.3333 | 644.0819
12 | 2.45 | 29.4 | 75 | 120 | 37.5 | 12 | 38.5501 | 35 | 112.3875 | 4.5 | 35 | 50.625 | 60 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 43.125 | #8 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 0.375 | 1279.5532 | 40 | 55 | 20 | 52.8 | 0.58667 | 0.29333 | 450 | 24 | 30 | 16 | 19.3333 | 917.0532
12 | 2.45 | 29.4 | 100 | 208 | 28.8462 | 12 | 38.5501 | 35 | 149.85 | 6 | 35 | 38.9423 | 40 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 33.1731 | #10 | 10 | 164.835 | #1 | 10 | 110 | #3 | 0.5 | 1706.071 | 40 | 55 | 20 | 70.4 | 0.78222 | 0.39111 | 450 | 24 | 30 | 16 | 19.3333 | 1343.571
12 | 2.45 | 29.4 | 125 | 208 | 34.8558 | 12 | 38.5501 | 35 | 187.3125 | 7.25 | 35 | 47.0553 | 50 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 40.0841 | #10 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 0.6125 | 2089.937 | 40 | 55 | 20 | 86.24 | 0.95822 | 0.47911 | 450 | 24 | 30 | 16 | 19.3333 | 1727.437
12 | 2.45 | 29.4 | 150 | 208 | 42.0673 | 12 | 38.5501 | 35 | 224.775 | 8.75 | 35 | 56.7909 | 60 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 48.3774 | #8 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 0.7375 | 2516.4547 | 40 | 55 | 20 | 103.84 | 1.1538 | 0.57689 | 450 | 24 | 30 | 16 | 19.3333 | 2153.9547
12 | 2.45 | 29.4 | 175 | 480 | 21.875 | 12 | 38.5501 | 35 | 262.2375 | 10.5 | 35 | 29.5313 | 30 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 25.1562 | #10 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 0.875 | 2985.6242 | 40 | 55 | 20 | 123.2 | 1.3689 | 0.68444 | 450 | 24 | 30 | 16 | 19.3333 | 2623.1242
12 | 2.45 | 29.4 | 200 | 480 | 25 | 12 | 38.5501 | 35 | 299.7 | 12 | 35 | 33.75 | 40 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 28.75 | #10 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 1 | 3412.142 | 40 | 55 | 20 | 140.8 | 1.5644 | 0.78222 | 450 | 24 | 30 | 16 | 19.3333 | 3049.642
12 | 2.45 | 29.4 | 250 | 480 | 30.2083 | 12 | 38.5501 | 35 | 374.625 | 14.5 | 35 | 40.7812 | 50 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 34.7396 | #10 | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 1.225 | 4179.874 | 40 | 55 | 20 | 172.48 | 1.9164 | 0.95822 | 450 | 24 | 30 | 16 | 19.3333 | 3817.374
12 | 2.45 | 29.4 | 300 | 480 | 36.4583 | 12 | 38.5501 | 35 | 449.55 | 17.5 | 35 | 49.2188 | 50 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 41.9271 | #8 | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 1.475 | 5032.9095 | 40 | 55 | 20 | 207.68 | 2.3076 | 1.1538 | 450 | 24 | 30 | 16 | 19.3333 | 4670.4095
12 | 2.45 | 29.4 | 350 | 480 | 43.75 | 12 | 38.5501 | 35 | 524.475 | 21 | 35 | 59.0625 | 60 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 50.3125 | #8 | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 1.75 | 5971.2485 | 40 | 55 | 20 | 246.4 | 2.7378 | 1.3689 | 450 | 24 | 30 | 16 | 19.3333 | 5608.7485
12 | 2.45 | 29.4 | 400 | 480 | 50 | 12 | 38.5501 | 35 | 599.4 | 24 | 35 | 67.5 | 70 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 57.5 | #8 | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 2 | 6824.284 | 40 | 55 | 20 | 281.6 | 3.1289 | 1.5644 | 450 | 24 | 30 | 16 | 19.3333 | 6461.784
12 | 2.45 | 29.4 | 450 | 480 | 54.1667 | 12 | 38.5501 | 35 | 674.325 | 26 | 35 | 73.125 | 80 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 62.2917 | #6 | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 2.2 | 7506.7124 | 40 | 55 | 20 | 309.76 | 3.4418 | 1.7209 | 450 | 24 | 30 | 16 | 19.3333 | 7144.2124
12 | 2.45 | 29.4 | 500 | 480 | 60.4167 | 12 | 38.5501 | 35 | 749.25 | 29 | 35 | 81.5625 | 90 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 69.4792 | #6 | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 2.45 | 8359.7479 | 40 | 55 | 20 | 344.96 | 3.8329 | 1.9164 | 450 | 24 | 30 | 16 | 19.3333 | 7997.2479
12 | 2.45 | 29.4 | 600 | 480 | 72.9167 | 12 | 38.5501 | 35 | 899.1 | 35 | 35 | 98.4375 | 100 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 83.8542 | #4 | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 2.95 | 10065.8189 | 40 | 55 | 20 | 415.36 | 4.6151 | 2.3076 | 450 | 24 | 30 | 16 | 19.3333 | 9703.3189
12 | 2.45 | 29.4 | 700 | 480 | 85.4167 | 12 | 38.5501 | 35 | 1048.95 | 41 | 35 | 115.3125 | 125 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 98.2292 | #4 | 10 | 1153.845 | Buss | 10 | 770 | Buss | 3.45 | 11771.8899 | 40 | 55 | 20 | 485.76 | 5.3973 | 2.6987 | 450 | 24 | 30 | 16 | 19.3333 | 11409.3899
12 | 2.45 | 29.4 | 800 | 480 | 97.9167 | 12 | 38.5501 | 35 | 1198.8 | 47 | 35 | 132.1875 | 150 | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 112.6042 | #3 | 10 | 1318.68 | Buss | 10 | 880 | Buss | 3.95 | 13477.9609 | 40 | 55 | 20 | 556.16 | 6.1796 | 3.0898 | 450 | 24 | 30 | 16 | 19.3333 | 13115.4609
12 | 2.45 | 29.4 | 900 | 480 | 108.3333 | 12 | 38.5501 | 35 | 1348.65 | 52 | 35 | 146.25 | 150 | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 124.5833 | #2 | 10 | 1483.515 | Buss | 10 | 990 | Buss | 4.4 | 15013.4248 | 40 | 55 | 20 | 619.52 | 6.8836 | 3.4418 | 450 | 24 | 30 | 16 | 19.3333 | 14650.9248
12 | 2.45 | 29.4 | 1000 | 480 | 120.8333 | 12 | 38.5501 | 35 | 1498.5 | 58 | 35 | 163.125 | 175 | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 138.9583 | #2 | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 4.9 | 16719.4958 | 40 | 55 | 20 | 689.92 | 7.6658 | 3.8329 | 450 | 24 | 30 | 16 | 19.3333 | 16356.9958
12 | 2.45 | 29.4 | 1100 | 480 | 133.3333 | 12 | 38.5501 | 35 | 1648.35 | 64 | 35 | 180 | 200 | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 153.3333 | #1 | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 5.4 | 18425.5668 | 40 | 55 | 20 | 760.32 | 8.448 | 4.224 | 450 | 24 | 30 | 16 | 19.3333 | 18063.0668
12 | 2.45 | 29.4 | 1200 | 480 | 145.8333 | 12 | 38.5501 | 35 | 1798.2 | 70 | 35 | 196.875 | 200 | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 167.7083 | #1/0 | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 5.9 | 20131.6378 | 40 | 55 | 20 | 830.72 | 9.2302 | 4.6151 | 450 | 24 | 30 | 16 | 19.3333 | 19769.1378
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
36 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
18 | 2.45 | 44.1 | 5 | 120 | 4.1667 | 12 | 56.8251 | 35 | 7.4925 | 0.5 | 35 | 5.625 | 10 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 4.7917 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.035 | 119.425 | 40 | 55 | 20 | 4.928 | 0.054756 | 0.027378 | 450 | 24 | 30 | 16 | 19.3333 | -243.075
18 | 2.45 | 44.1 | 10 | 120 | 8.3333 | 12 | 56.8251 | 35 | 14.985 | 1 | 35 | 11.25 | 15 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 9.5833 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.07 | 238.8499 | 40 | 55 | 20 | 9.856 | 0.10951 | 0.054756 | 450 | 24 | 30 | 16 | 19.3333 | -123.6501
18 | 2.45 | 44.1 | 15 | 120 | 12.5 | 12 | 56.8251 | 35 | 22.4775 | 1.5 | 35 | 16.875 | 20 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 14.375 | #10 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.105 | 358.2749 | 40 | 55 | 20 | 14.784 | 0.16427 | 0.082133 | 600 | 24 | 48 | 16 | 29.3333 | -191.7251
18 | 2.45 | 44.1 | 20 | 120 | 14.5833 | 12 | 56.8251 | 35 | 29.97 | 1.75 | 35 | 19.6875 | 20 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 16.7708 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.1275 | 435.0481 | 40 | 55 | 20 | 17.952 | 0.19947 | 0.099733 | 600 | 24 | 48 | 16 | 29.3333 | -114.9519
18 | 2.45 | 44.1 | 25 | 120 | 18.75 | 12 | 56.8251 | 35 | 37.4625 | 2.25 | 35 | 25.3125 | 30 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 21.5625 | #10 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.1625 | 554.4731 | 40 | 55 | 20 | 22.88 | 0.25422 | 0.12711 | 600 | 24 | 48 | 16 | 29.3333 | 4.4731
18 | 2.45 | 44.1 | 30 | 120 | 22.9167 | 12 | 56.8251 | 35 | 44.955 | 2.75 | 35 | 30.9375 | 40 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 26.3542 | #10 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.1975 | 673.898 | 40 | 55 | 20 | 27.808 | 0.30898 | 0.15449 | 600 | 24 | 48 | 16 | 29.3333 | 123.898
18 | 2.45 | 44.1 | 35 | 120 | 25 | 12 | 56.8251 | 35 | 52.4475 | 3 | 35 | 33.75 | 40 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 28.75 | #10 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 0.22 | 750.6712 | 40 | 55 | 20 | 30.976 | 0.34418 | 0.17209 | 600 | 24 | 48 | 16 | 29.3333 | 200.6712
18 | 2.45 | 44.1 | 40 | 120 | 29.1667 | 12 | 56.8251 | 35 | 59.94 | 3.5 | 35 | 39.375 | 40 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 33.5417 | #10 | 10 | 65.934 | #6 | 10 | 44 | #8 | 0.255 | 870.0962 | 40 | 55 | 20 | 35.904 | 0.39893 | 0.19947 | 600 | 24 | 48 | 16 | 29.3333 | 320.0962
18 | 2.45 | 44.1 | 50 | 120 | 37.5 | 12 | 56.8251 | 35 | 74.925 | 4.5 | 35 | 50.625 | 60 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 43.125 | #8 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 0.325 | 1108.9461 | 40 | 55 | 20 | 45.76 | 0.50844 | 0.25422 | 800 | 34 | 48 | 28 | 47.9444 | 209.9878
18 | 2.45 | 44.1 | 60 | 208 | 25.2404 | 12 | 56.8251 | 35 | 89.91 | 5.25 | 35 | 34.0745 | 40 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 29.0264 | #10 | 10 | 98.901 | #4 | 10 | 66 | #6 | 0.3825 | 1305.1443 | 40 | 55 | 20 | 53.856 | 0.5984 | 0.2992 | 800 | 34 | 48 | 28 | 47.9444 | 406.186
18 | 2.45 | 44.1 | 75 | 208 | 31.25 | 12 | 56.8251 | 35 | 112.3875 | 6.5 | 35 | 42.1875 | 50 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 35.9375 | #10 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 0.475 | 1620.7674 | 40 | 55 | 20 | 66.88 | 0.74311 | 0.37156 | 800 | 34 | 48 | 28 | 47.9444 | 721.8091
18 | 2.45 | 44.1 | 100 | 208 | 42.0673 | 12 | 56.8251 | 35 | 149.85 | 8.75 | 35 | 56.7909 | 60 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 48.3774 | #8 | 10 | 164.835 | #1 | 10 | 110 | #3 | 0.6375 | 2175.2405 | 40 | 55 | 20 | 89.76 | 0.99733 | 0.49867 | 800 | 34 | 48 | 28 | 47.9444 | 1276.2822
18 | 2.45 | 44.1 | 125 | 480 | 22.9167 | 12 | 56.8251 | 35 | 187.3125 | 11 | 35 | 30.9375 | 40 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 26.3542 | #10 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 0.8 | 2729.7136 | 40 | 55 | 20 | 112.64 | 1.2516 | 0.62578 | 800 | 34 | 48 | 28 | 47.9444 | 1830.7553
18 | 2.45 | 44.1 | 150 | 480 | 27.0833 | 12 | 56.8251 | 35 | 224.775 | 13 | 35 | 36.5625 | 40 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 31.1458 | #10 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 0.95 | 3241.5349 | 40 | 55 | 20 | 133.76 | 1.4862 | 0.74311 | 800 | 34 | 48 | 28 | 47.9444 | 2342.5766
18 | 2.45 | 44.1 | 175 | 480 | 31.25 | 12 | 56.8251 | 35 | 262.2375 | 15 | 35 | 42.1875 | 50 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 35.9375 | #10 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 1.1 | 3753.3562 | 40 | 55 | 20 | 154.88 | 1.7209 | 0.86044 | 1200 | 38 | 70 | 28 | 71.5556 | 2411.6895
18 | 2.45 | 44.1 | 200 | 480 | 36.4583 | 12 | 56.8251 | 35 | 299.7 | 17.5 | 35 | 49.2188 | 50 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 41.9271 | #8 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 1.275 | 4350.481 | 40 | 55 | 20 | 179.52 | 1.9947 | 0.99733 | 1200 | 38 | 70 | 28 | 71.5556 | 3008.8144
18 | 2.45 | 44.1 | 250 | 480 | 45.8333 | 12 | 56.8251 | 35 | 374.625 | 22 | 35 | 61.875 | 60 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 52.7083 | #8 | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 1.6 | 5459.4272 | 40 | 55 | 20 | 225.28 | 2.5031 | 1.2516 | 1200 | 38 | 70 | 28 | 71.5556 | 4117.7605
18 | 2.45 | 44.1 | 300 | 480 | 54.1667 | 12 | 56.8251 | 35 | 449.55 | 26 | 35 | 73.125 | 80 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 62.2917 | #6 | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 1.9 | 6483.0698 | 40 | 55 | 20 | 267.52 | 2.9724 | 1.4862 | 1200 | 38 | 70 | 28 | 71.5556 | 5141.4031
18 | 2.45 | 44.1 | 350 | 480 | 62.5 | 12 | 56.8251 | 35 | 524.475 | 30 | 35 | 84.375 | 90 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 71.875 | #6 | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 2.2 | 7506.7124 | 40 | 55 | 20 | 309.76 | 3.4418 | 1.7209 | 1200 | 38 | 70 | 28 | 71.5556 | 6165.0457
18 | 2.45 | 44.1 | 400 | 480 | 72.9167 | 12 | 56.8251 | 35 | 599.4 | 35 | 35 | 98.4375 | 100 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 83.8542 | #4 | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 2.55 | 8700.9621 | 40 | 55 | 20 | 359.04 | 3.9893 | 1.9947 | 1200 | 38 | 70 | 28 | 71.5556 | 7359.2954
18 | 2.45 | 44.1 | 450 | 480 | 81.25 | 12 | 56.8251 | 35 | 674.325 | 39 | 35 | 109.6875 | 110 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 93.4375 | #4 | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 2.85 | 9724.6047 | 40 | 55 | 20 | 401.28 | 4.4587 | 2.2293 | 1200 | 38 | 70 | 28 | 71.5556 | 8382.938
18 | 2.45 | 44.1 | 500 | 480 | 89.5833 | 12 | 56.8251 | 35 | 749.25 | 43 | 35 | 120.9375 | 125 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 103.0208 | #4 | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 3.15 | 10748.2473 | 40 | 55 | 20 | 443.52 | 4.928 | 2.464 | 1200 | 38 | 70 | 28 | 71.5556 | 9406.5806
18 | 2.45 | 44.1 | 600 | 480 | 108.3333 | 12 | 56.8251 | 35 | 899.1 | 52 | 35 | 146.25 | 150 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 124.5833 | #2 | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 3.8 | 12966.1396 | 40 | 55 | 20 | 535.04 | 5.9449 | 2.9724 | 1200 | 38 | 70 | 28 | 71.5556 | 11624.4729
18 | 2.45 | 44.1 | 700 | 480 | 125 | 12 | 56.8251 | 35 | 1048.95 | 60 | 35 | 168.75 | 175 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 143.75 | #1 | 10 | 1153.845 | Buss | 10 | 770 | Buss | 4.4 | 15013.4248 | 40 | 55 | 20 | 619.52 | 6.8836 | 3.4418 | 1200 | 38 | 70 | 28 | 71.5556 | 13671.7581
18 | 2.45 | 44.1 | 800 | 480 | 143.75 | 12 | 56.8251 | 35 | 1198.8 | 69 | 35 | 194.0625 | 200 | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 165.3125 | #1 | 10 | 1318.68 | Buss | 10 | 880 | Buss | 5.05 | 17231.3171 | 40 | 55 | 20 | 711.04 | 7.9004 | 3.9502 | 1200 | 38 | 70 | 28 | 71.5556 | 15889.6504
18 | 2.45 | 44.1 | 900 | 480 | 160.4167 | 12 | 56.8251 | 35 | 1348.65 | 77 | 35 | 216.5625 | 225 | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 184.4792 | #1/0 | 10 | 1483.515 | Buss | 10 | 990 | Buss | 5.65 | 19278.6023 | 40 | 55 | 20 | 795.52 | 8.8391 | 4.4196 | 1200 | 38 | 70 | 28 | 71.5556 | 17936.9356
18 | 2.45 | 44.1 | 1000 | 480 | 179.1667 | 12 | 56.8251 | 35 | 1498.5 | 86 | 35 | 241.875 | 250 | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 206.0417 | #2/0 | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 6.3 | 21496.4946 | 40 | 55 | 20 | 887.04 | 9.856 | 4.928 | 1200 | 38 | 70 | 28 | 71.5556 | 20154.8279
18 | 2.45 | 44.1 | 1100 | 480 | 195.8333 | 12 | 56.8251 | 35 | 1648.35 | 94 | 35 | 264.375 | 300 | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 225.2083 | #2/0 | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 6.9 | 23543.7798 | 40 | 55 | 20 | 971.52 | 10.7947 | 5.3973 | 1200 | 38 | 70 | 28 | 71.5556 | 22202.1131
18 | 2.45 | 44.1 | 1200 | 480 | 214.5833 | 12 | 56.8251 | 35 | 1798.2 | 103 | 35 | 289.6875 | 300 | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 246.7708 | #3/0 | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 7.55 | 25761.6721 | 40 | 55 | 20 | 1063.04 | 11.8116 | 5.9058 | 1200 | 38 | 70 | 28 | 71.5556 | 24420.0054
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
48 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
24 | 2.45 | 58.8 | 5 | 120 | 6.25 | 12 | 75.1002 | 35 | 7.4925 | 0.75 | 35 | 8.4375 | 10 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 7.1875 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.0475 | 162.0767 | 40 | 55 | 20 | 6.688 | 0.074311 | 0.037156 | 450 | 24 | 30 | 16 | 19.3333 | -200.4233
24 | 2.45 | 58.8 | 10 | 120 | 10.4167 | 12 | 75.1002 | 35 | 14.985 | 1.25 | 35 | 14.0625 | 15 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 11.9792 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.0825 | 281.5017 | 40 | 55 | 20 | 11.616 | 0.12907 | 0.064533 | 450 | 24 | 30 | 16 | 19.3333 | -80.9983
24 | 2.45 | 58.8 | 15 | 120 | 14.5833 | 12 | 75.1002 | 35 | 22.4775 | 1.75 | 35 | 19.6875 | 20 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 16.7708 | #10 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.1175 | 400.9267 | 40 | 55 | 20 | 16.544 | 0.18382 | 0.091911 | 600 | 24 | 48 | 16 | 29.3333 | -149.0733
24 | 2.45 | 58.8 | 20 | 120 | 20.8333 | 12 | 75.1002 | 35 | 29.97 | 2.5 | 35 | 28.125 | 30 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 23.9583 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.165 | 563.0034 | 40 | 55 | 20 | 23.232 | 0.25813 | 0.12907 | 600 | 24 | 48 | 16 | 29.3333 | 13.0034
24 | 2.45 | 58.8 | 25 | 120 | 25 | 12 | 75.1002 | 35 | 37.4625 | 3 | 35 | 33.75 | 40 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 28.75 | #10 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.2 | 682.4284 | 40 | 55 | 20 | 28.16 | 0.31289 | 0.15644 | 600 | 24 | 48 | 16 | 29.3333 | 132.4284
24 | 2.45 | 58.8 | 30 | 120 | 29.1667 | 12 | 75.1002 | 35 | 44.955 | 3.5 | 35 | 39.375 | 40 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 33.5417 | #10 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.235 | 801.8534 | 40 | 55 | 20 | 33.088 | 0.36764 | 0.18382 | 600 | 24 | 48 | 16 | 29.3333 | 251.8534
24 | 2.45 | 58.8 | 35 | 120 | 33.3333 | 12 | 75.1002 | 35 | 52.4475 | 4 | 35 | 45 | 50 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 38.3333 | #10 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 0.27 | 921.2783 | 40 | 55 | 20 | 38.016 | 0.4224 | 0.2112 | 600 | 24 | 48 | 16 | 29.3333 | 371.2783
24 | 2.45 | 58.8 | 40 | 120 | 39.5833 | 12 | 75.1002 | 35 | 59.94 | 4.75 | 35 | 53.4375 | 60 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 45.5208 | #8 | 10 | 65.934 | #6 | 10 | 44 | #8 | 0.3175 | 1083.3551 | 40 | 55 | 20 | 44.704 | 0.49671 | 0.24836 | 600 | 24 | 48 | 16 | 29.3333 | 533.3551
24 | 2.45 | 58.8 | 50 | 208 | 27.6442 | 12 | 75.1002 | 35 | 74.925 | 5.75 | 35 | 37.3197 | 40 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 31.7909 | #10 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 0.3875 | 1322.205 | 40 | 55 | 20 | 54.56 | 0.60622 | 0.30311 | 800 | 34 | 48 | 28 | 47.9444 | 423.2467
24 | 2.45 | 58.8 | 60 | 208 | 33.6538 | 12 | 75.1002 | 35 | 89.91 | 7 | 35 | 45.4327 | 50 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 38.7019 | #10 | 10 | 98.901 | #4 | 10 | 66 | #6 | 0.47 | 1603.7067 | 40 | 55 | 20 | 66.176 | 0.73529 | 0.36764 | 800 | 34 | 48 | 28 | 47.9444 | 704.7484
24 | 2.45 | 58.8 | 75 | 208 | 40.8654 | 12 | 75.1002 | 35 | 112.3875 | 8.5 | 35 | 55.1683 | 60 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 46.9952 | #8 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 0.575 | 1961.9816 | 40 | 55 | 20 | 80.96 | 0.89956 | 0.44978 | 800 | 34 | 48 | 28 | 47.9444 | 1063.0233
24 | 2.45 | 58.8 | 100 | 480 | 23.9583 | 12 | 75.1002 | 35 | 149.85 | 11.5 | 35 | 32.3438 | 40 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 27.5521 | #10 | 10 | 164.835 | #1 | 10 | 110 | #3 | 0.775 | 2644.4101 | 40 | 55 | 20 | 109.12 | 1.2124 | 0.60622 | 800 | 34 | 48 | 28 | 47.9444 | 1745.4517
24 | 2.45 | 58.8 | 125 | 480 | 30.2083 | 12 | 75.1002 | 35 | 187.3125 | 14.5 | 35 | 40.7812 | 50 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 34.7396 | #10 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 0.975 | 3326.8384 | 40 | 55 | 20 | 137.28 | 1.5253 | 0.76267 | 800 | 34 | 48 | 28 | 47.9444 | 2427.8801
24 | 2.45 | 58.8 | 150 | 480 | 35.4167 | 12 | 75.1002 | 35 | 224.775 | 17 | 35 | 47.8125 | 50 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 40.7292 | #8 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 1.15 | 3923.9633 | 40 | 55 | 20 | 161.92 | 1.7991 | 0.89956 | 800 | 34 | 48 | 28 | 47.9444 | 3025.005
24 | 2.45 | 58.8 | 175 | 480 | 41.6667 | 12 | 75.1002 | 35 | 262.2375 | 20 | 35 | 56.25 | 60 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 47.9167 | #8 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 1.35 | 4606.3917 | 40 | 55 | 20 | 190.08 | 2.112 | 1.056 | 1200 | 38 | 70 | 28 | 71.5556 | 3264.725
24 | 2.45 | 58.8 | 200 | 480 | 47.9167 | 12 | 75.1002 | 35 | 299.7 | 23 | 35 | 64.6875 | 70 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 55.1042 | #8 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 1.55 | 5288.8201 | 40 | 55 | 20 | 218.24 | 2.4249 | 1.2124 | 1200 | 38 | 70 | 28 | 71.5556 | 3947.1534
24 | 2.45 | 58.8 | 250 | 480 | 60.4167 | 12 | 75.1002 | 35 | 374.625 | 29 | 35 | 81.5625 | 90 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 69.4792 | #6 | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 1.95 | 6653.6769 | 40 | 55 | 20 | 274.56 | 3.0507 | 1.5253 | 1200 | 38 | 70 | 28 | 71.5556 | 5312.0102
24 | 2.45 | 58.8 | 300 | 480 | 70.8333 | 12 | 75.1002 | 35 | 449.55 | 34 | 35 | 95.625 | 100 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 81.4583 | #4 | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 2.3 | 7847.9266 | 40 | 55 | 20 | 323.84 | 3.5982 | 1.7991 | 1200 | 38 | 70 | 28 | 71.5556 | 6506.2599
24 | 2.45 | 58.8 | 350 | 480 | 83.3333 | 12 | 75.1002 | 35 | 524.475 | 40 | 35 | 112.5 | 125 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 95.8333 | #4 | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 2.7 | 9212.7834 | 40 | 55 | 20 | 380.16 | 4.224 | 2.112 | 1200 | 38 | 70 | 28 | 71.5556 | 7871.1167
24 | 2.45 | 58.8 | 400 | 480 | 95.8333 | 12 | 75.1002 | 35 | 599.4 | 46 | 35 | 129.375 | 150 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 110.2083 | #3 | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 3.1 | 10577.6402 | 40 | 55 | 20 | 436.48 | 4.8498 | 2.4249 | 1200 | 38 | 70 | 28 | 71.5556 | 9235.9735
24 | 2.45 | 58.8 | 450 | 480 | 106.25 | 12 | 75.1002 | 35 | 674.325 | 51 | 35 | 143.4375 | 150 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 122.1875 | #2 | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 3.45 | 11771.8899 | 40 | 55 | 20 | 485.76 | 5.3973 | 2.6987 | 1200 | 38 | 70 | 28 | 71.5556 | 10430.2232
24 | 2.45 | 58.8 | 500 | 480 | 118.75 | 12 | 75.1002 | 35 | 749.25 | 57 | 35 | 160.3125 | 175 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 136.5625 | #2 | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 3.85 | 13136.7467 | 40 | 55 | 20 | 542.08 | 6.0231 | 3.0116 | 1200 | 38 | 70 | 28 | 71.5556 | 11795.08
24 | 2.45 | 58.8 | 600 | 480 | 141.6667 | 12 | 75.1002 | 35 | 899.1 | 68 | 35 | 191.25 | 200 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 162.9167 | #1 | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 4.6 | 15695.8532 | 40 | 55 | 20 | 647.68 | 7.1964 | 3.5982 | 1200 | 38 | 70 | 28 | 71.5556 | 14354.1865
24 | 2.45 | 58.8 | 700 | 480 | 164.5833 | 12 | 75.1002 | 35 | 1048.95 | 79 | 35 | 222.1875 | 225 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 189.2708 | #1/0 | 10 | 1153.845 | Buss | 10 | 770 | Buss | 5.35 | 18254.9597 | 40 | 55 | 20 | 753.28 | 8.3698 | 4.1849 | 1200 | 38 | 70 | 28 | 71.5556 | 16913.293
24 | 2.45 | 58.8 | 800 | 480 | 189.5833 | 12 | 75.1002 | 35 | 1198.8 | 91 | 35 | 255.9375 | 300 | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 218.0208 | #2/0 | 10 | 1318.68 | Buss | 10 | 880 | Buss | 6.15 | 20984.6733 | 40 | 55 | 20 | 865.92 | 9.6213 | 4.8107 | 1200 | 38 | 70 | 28 | 71.5556 | 19643.0066
24 | 2.45 | 58.8 | 900 | 480 | 212.5 | 12 | 75.1002 | 35 | 1348.65 | 102 | 35 | 286.875 | 300 | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 244.375 | #3/0 | 10 | 1483.515 | Buss | 10 | 990 | Buss | 6.9 | 23543.7798 | 40 | 55 | 20 | 971.52 | 10.7947 | 5.3973 | 1200 | 38 | 70 | 28 | 71.5556 | 22202.1131
24 | 2.45 | 58.8 | 1000 | 480 | 235.4167 | 12 | 75.1002 | 35 | 1498.5 | 113 | 35 | 317.8125 | 350 | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 270.7292 | #4/0 | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 7.65 | 26102.8863 | 40 | 55 | 20 | 1077.12 | 11.968 | 5.984 | 1200 | 38 | 70 | 28 | 71.5556 | 24761.2196
24 | 2.45 | 58.8 | 1100 | 480 | 258.3333 | 12 | 75.1002 | 35 | 1648.35 | 124 | 35 | 348.75 | 350 | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 297.0833 | #4/0 | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 8.4 | 28661.9928 | 40 | 55 | 20 | 1182.72 | 13.1413 | 6.5707 | 1200 | 38 | 70 | 28 | 71.5556 | 27320.3261
24 | 2.45 | 58.8 | 1200 | 480 | 283.3333 | 12 | 75.1002 | 35 | 1798.2 | 136 | 35 | 382.5 | 400 | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 325.8333 | 250MCM | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 9.2 | 31391.7064 | 40 | 55 | 20 | 1295.36 | 14.3929 | 7.1964 | 1200 | 38 | 70 | 28 | 71.5556 | 30050.0397
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
72 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
36 | 2.45 | 88.2 | 5 | 120 | 8.3333 | 12 | 109.6502 | 35 | 7.4925 | 1 | 35 | 11.25 | 15 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 9.5833 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.06 | 204.7285 | 40 | 55 | 20 | 8.448 | 0.093867 | 0.046933 | 450 | 24 | 30 | 16 | 19.3333 | -157.7715
36 | 2.45 | 88.2 | 10 | 120 | 14.5833 | 12 | 109.6502 | 35 | 14.985 | 1.75 | 35 | 19.6875 | 20 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 16.7708 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.1075 | 366.8053 | 40 | 55 | 20 | 15.136 | 0.16818 | 0.084089 | 450 | 24 | 30 | 16 | 19.3333 | 4.3053
36 | 2.45 | 88.2 | 15 | 120 | 20.8333 | 12 | 109.6502 | 35 | 22.4775 | 2.5 | 35 | 28.125 | 30 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 23.9583 | #10 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.155 | 528.882 | 40 | 55 | 20 | 21.824 | 0.24249 | 0.12124 | 600 | 24 | 48 | 16 | 29.3333 | -21.118
36 | 2.45 | 88.2 | 20 | 120 | 29.1667 | 12 | 109.6502 | 35 | 29.97 | 3.5 | 35 | 39.375 | 40 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 33.5417 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.215 | 733.6105 | 40 | 55 | 20 | 30.272 | 0.33636 | 0.16818 | 600 | 24 | 48 | 16 | 29.3333 | 183.6105
36 | 2.45 | 88.2 | 25 | 120 | 35.4167 | 12 | 109.6502 | 35 | 37.4625 | 4.25 | 35 | 47.8125 | 50 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 40.7292 | #8 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.2625 | 895.6873 | 40 | 55 | 20 | 36.96 | 0.41067 | 0.20533 | 600 | 24 | 48 | 16 | 29.3333 | 345.6873
36 | 2.45 | 88.2 | 30 | 120 | 41.6667 | 12 | 109.6502 | 35 | 44.955 | 5 | 35 | 56.25 | 60 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 47.9167 | #8 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.31 | 1057.764 | 40 | 55 | 20 | 43.648 | 0.48498 | 0.24249 | 600 | 24 | 48 | 16 | 29.3333 | 507.764
36 | 2.45 | 88.2 | 35 | 208 | 28.8462 | 12 | 109.6502 | 35 | 52.4475 | 6 | 35 | 38.9423 | 40 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 33.1731 | #10 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 0.37 | 1262.4925 | 40 | 55 | 20 | 52.096 | 0.57884 | 0.28942 | 600 | 24 | 48 | 16 | 29.3333 | 712.4925
36 | 2.45 | 88.2 | 40 | 208 | 32.4519 | 12 | 109.6502 | 35 | 59.94 | 6.75 | 35 | 43.8101 | 50 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 37.3197 | #10 | 10 | 65.934 | #6 | 10 | 44 | #8 | 0.4175 | 1424.5693 | 40 | 55 | 20 | 58.784 | 0.65316 | 0.32658 | 600 | 24 | 48 | 16 | 29.3333 | 874.5693
36 | 2.45 | 88.2 | 50 | 208 | 39.6635 | 12 | 109.6502 | 35 | 74.925 | 8.25 | 35 | 53.5457 | 60 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 45.613 | #8 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 0.5125 | 1748.7228 | 40 | 55 | 20 | 72.16 | 0.80178 | 0.40089 | 800 | 34 | 48 | 28 | 47.9444 | 849.7644
36 | 2.45 | 88.2 | 60 | 240 | 41.6667 | 12 | 109.6502 | 35 | 89.91 | 10 | 35 | 56.25 | 60 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 47.9167 | #8 | 10 | 98.901 | #4 | 10 | 66 | #6 | 0.62 | 2115.528 | 40 | 55 | 20 | 87.296 | 0.96996 | 0.48498 | 800 | 34 | 48 | 28 | 47.9444 | 1216.5697
36 | 2.45 | 88.2 | 75 | 480 | 26.0417 | 12 | 109.6502 | 35 | 112.3875 | 12.5 | 35 | 35.1563 | 40 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 29.9479 | #10 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 0.775 | 2644.41 | 40 | 55 | 20 | 109.12 | 1.2124 | 0.60622 | 800 | 34 | 48 | 28 | 47.9444 | 1745.4517
36 | 2.45 | 88.2 | 100 | 480 | 34.375 | 12 | 109.6502 | 35 | 149.85 | 16.5 | 35 | 46.4062 | 50 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 39.5312 | #10 | 10 | 164.835 | #1 | 10 | 110 | #3 | 1.025 | 3497.4455 | 40 | 55 | 20 | 144.32 | 1.6036 | 0.80178 | 800 | 34 | 48 | 28 | 47.9444 | 2598.4872
36 | 2.45 | 88.2 | 125 | 480 | 43.75 | 12 | 109.6502 | 35 | 187.3125 | 21 | 35 | 59.0625 | 60 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 50.3125 | #8 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 1.3 | 4435.7846 | 40 | 55 | 20 | 183.04 | 2.0338 | 1.0169 | 800 | 34 | 48 | 28 | 47.9444 | 3536.8263
36 | 2.45 | 88.2 | 150 | 480 | 52.0833 | 12 | 109.6502 | 35 | 224.775 | 25 | 35 | 70.3125 | 80 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 59.8958 | #8 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 1.55 | 5288.8201 | 40 | 55 | 20 | 218.24 | 2.4249 | 1.2124 | 800 | 34 | 48 | 28 | 47.9444 | 4389.8618
36 | 2.45 | 88.2 | 175 | 480 | 60.4167 | 12 | 109.6502 | 35 | 262.2375 | 29 | 35 | 81.5625 | 90 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 69.4792 | #6 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 1.8 | 6141.8556 | 40 | 55 | 20 | 253.44 | 2.816 | 1.408 | 1200 | 38 | 70 | 28 | 71.5556 | 4800.1889
36 | 2.45 | 88.2 | 200 | 480 | 68.75 | 12 | 109.6502 | 35 | 299.7 | 33 | 35 | 92.8125 | 100 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 79.0625 | #6 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 2.05 | 6994.8911 | 40 | 55 | 20 | 288.64 | 3.2071 | 1.6036 | 1200 | 38 | 70 | 28 | 71.5556 | 5653.2244
36 | 2.45 | 88.2 | 250 | 480 | 87.5 | 12 | 109.6502 | 35 | 374.625 | 42 | 35 | 118.125 | 125 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 100.625 | #4 | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 2.6 | 8871.5692 | 40 | 55 | 20 | 366.08 | 4.0676 | 2.0338 | 1200 | 38 | 70 | 28 | 71.5556 | 7529.9025
36 | 2.45 | 88.2 | 300 | 480 | 104.1667 | 12 | 109.6502 | 35 | 449.55 | 50 | 35 | 140.625 | 150 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 119.7917 | #3 | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 3.1 | 10577.6402 | 40 | 55 | 20 | 436.48 | 4.8498 | 2.4249 | 1200 | 38 | 70 | 28 | 71.5556 | 9235.9735
36 | 2.45 | 88.2 | 350 | 480 | 120.8333 | 12 | 109.6502 | 35 | 524.475 | 58 | 35 | 163.125 | 175 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 138.9583 | #2 | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 3.6 | 12283.7112 | 40 | 55 | 20 | 506.88 | 5.632 | 2.816 | 1200 | 38 | 70 | 28 | 71.5556 | 10942.0445
36 | 2.45 | 88.2 | 400 | 480 | 137.5 | 12 | 109.6502 | 35 | 599.4 | 66 | 35 | 185.625 | 200 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 158.125 | #1 | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 4.1 | 13989.7822 | 40 | 55 | 20 | 577.28 | 6.4142 | 3.2071 | 1200 | 38 | 70 | 28 | 71.5556 | 12648.1155
36 | 2.45 | 88.2 | 450 | 480 | 154.1667 | 12 | 109.6502 | 35 | 674.325 | 74 | 35 | 208.125 | 225 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 177.2917 | #1/0 | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 4.6 | 15695.8532 | 40 | 55 | 20 | 647.68 | 7.1964 | 3.5982 | 1200 | 38 | 70 | 28 | 71.5556 | 14354.1865
36 | 2.45 | 88.2 | 500 | 480 | 172.9167 | 12 | 109.6502 | 35 | 749.25 | 83 | 35 | 233.4375 | 250 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 198.8542 | #2/0 | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 5.15 | 17572.5313 | 40 | 55 | 20 | 725.12 | 8.0569 | 4.0284 | 1200 | 38 | 70 | 28 | 71.5556 | 16230.8646
36 | 2.45 | 88.2 | 600 | 480 | 206.25 | 12 | 109.6502 | 35 | 899.1 | 99 | 35 | 278.4375 | 300 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 237.1875 | #3/0 | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 6.15 | 20984.6733 | 40 | 55 | 20 | 865.92 | 9.6213 | 4.8107 | 1200 | 38 | 70 | 28 | 71.5556 | 19643.0066
36 | 2.45 | 88.2 | 700 | 480 | 241.6667 | 12 | 109.6502 | 35 | 1048.95 | 116 | 35 | 326.25 | 350 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 277.9167 | #4/0 | 10 | 1153.845 | Buss | 10 | 770 | Buss | 7.2 | 24567.4224 | 40 | 55 | 20 | 1013.76 | 11.264 | 5.632 | 1200 | 38 | 70 | 28 | 71.5556 | 23225.7557
36 | 2.45 | 88.2 | 800 | 480 | 275 | 12 | 109.6502 | 35 | 1198.8 | 132 | 35 | 371.25 | 400 | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 316.25 | 250MCM | 10 | 1318.68 | Buss | 10 | 880 | Buss | 8.2 | 27979.5644 | 40 | 55 | 20 | 1154.56 | 12.8284 | 6.4142 | 1200 | 38 | 70 | 28 | 71.5556 | 26637.8977
36 | 2.45 | 88.2 | 900 | 480 | 308.3333 | 12 | 109.6502 | 35 | 1348.65 | 148 | 35 | 416.25 | 450 | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 354.5833 | 300MCM | 10 | 1483.515 | Buss | 10 | 990 | Buss | 9.2 | 31391.7064 | 40 | 55 | 20 | 1295.36 | 14.3929 | 7.1964 | 1200 | 38 | 70 | 28 | 71.5556 | 30050.0397
36 | 2.45 | 88.2 | 1000 | 480 | 343.75 | 12 | 109.6502 | 35 | 1498.5 | 165 | 35 | 464.0625 | 500 | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 395.3125 | #2/0 2x | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 10.25 | 34974.4555 | 40 | 55 | 20 | 1443.2 | 16.0356 | 8.0178 | 1200 | 38 | 70 | 28 | 71.5556 | 33632.7888
36 | 2.45 | 88.2 | 1100 | 480 | 377.0833 | 12 | 109.6502 | 35 | 1648.35 | 181 | 35 | 509.0625 | 600 | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 433.6458 | #2/0 2x | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 11.25 | 38386.5975 | 40 | 55 | 20 | 1584 | 17.6 | 8.8 | 1200 | 38 | 70 | 28 | 71.5556 | 37044.9308
36 | 2.45 | 88.2 | 1200 | 480 | 412.5 | 12 | 109.6502 | 35 | 1798.2 | 198 | 35 | 556.875 | 600 | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 474.375 | #3/0 2x | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 12.3 | 41969.3466 | 40 | 55 | 20 | 1731.84 | 19.2427 | 9.6213 | 1200 | 38 | 70 | 28 | 71.5556 | 40627.6799
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
120 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
60 | 2.45 | 147 | 5.5 | 120 | 14.5833 | 12 | 182.7504 | 35 | 8.2418 | 1.75 | 35 | 19.6875 | 20 | 30 | 10.7143 | 15 | 30 | 7.15 | 10 | 15 | 16.7708 | #10 | 10 | 9.0659 | #10 | 10 | 6.05 | #10 | 0.0985 | 336.096 | 40 | 55 | 20 | 13.8688 | 0.1541 | 0.077049 | 450 | 24 | 30 | 16 | 19.3333 | -26.404
60 | 2.45 | 147 | 10 | 240 | 11.4583 | 12 | 182.7504 | 35 | 14.985 | 2.75 | 35 | 15.4688 | 20 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 13.1771 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.1575 | 537.4124 | 40 | 55 | 20 | 22.176 | 0.2464 | 0.1232 | 450 | 24 | 30 | 16 | 19.3333 | 174.9124
60 | 2.45 | 147 | 15 | 120 | 35.4167 | 12 | 182.7504 | 35 | 22.4775 | 4.25 | 35 | 47.8125 | 50 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 40.7292 | #8 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.2425 | 827.4444 | 40 | 55 | 20 | 34.144 | 0.37938 | 0.18969 | 600 | 24 | 48 | 16 | 29.3333 | 277.4444
60 | 2.45 | 147 | 20 | 208 | 26.4423 | 12 | 182.7504 | 35 | 29.97 | 5.5 | 35 | 35.6971 | 40 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 30.4087 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.315 | 1074.8247 | 40 | 55 | 20 | 44.352 | 0.4928 | 0.2464 | 600 | 24 | 48 | 16 | 29.3333 | 524.8247
60 | 2.45 | 147 | 25 | 208 | 33.6538 | 12 | 182.7504 | 35 | 37.4625 | 7 | 35 | 45.4327 | 50 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 38.7019 | #10 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.4 | 1364.8568 | 40 | 55 | 20 | 56.32 | 0.62578 | 0.31289 | 600 | 24 | 48 | 16 | 29.3333 | 814.8568
60 | 2.45 | 147 | 30 | 240 | 34.375 | 12 | 182.7504 | 35 | 44.955 | 8.25 | 35 | 46.4062 | 50 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 39.5312 | #10 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.4725 | 1612.2371 | 40 | 55 | 20 | 66.528 | 0.7392 | 0.3696 | 600 | 24 | 48 | 16 | 29.3333 | 1062.2371
60 | 2.45 | 147 | 35 | 240 | 40.625 | 12 | 182.7504 | 35 | 52.4475 | 9.75 | 35 | 54.8438 | 60 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 46.7187 | #8 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 0.5575 | 1902.2692 | 40 | 55 | 20 | 78.496 | 0.87218 | 0.43609 | 600 | 24 | 48 | 16 | 29.3333 | 1352.2692
60 | 2.45 | 147 | 40 | 480 | 22.9167 | 12 | 182.7504 | 35 | 59.94 | 11 | 35 | 30.9375 | 40 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 26.3542 | #10 | 10 | 65.934 | #6 | 10 | 44 | #8 | 0.63 | 2149.6495 | 40 | 55 | 20 | 88.704 | 0.9856 | 0.4928 | 600 | 24 | 48 | 16 | 29.3333 | 1599.6495
60 | 2.45 | 147 | 50 | 480 | 29.1667 | 12 | 182.7504 | 35 | 74.925 | 14 | 35 | 39.375 | 40 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 33.5417 | #10 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 0.8 | 2729.7136 | 40 | 55 | 20 | 112.64 | 1.2516 | 0.62578 | 800 | 34 | 48 | 28 | 47.9444 | 1830.7553
60 | 2.45 | 147 | 60 | 480 | 34.375 | 12 | 182.7504 | 35 | 89.91 | 16.5 | 35 | 46.4062 | 50 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 39.5312 | #10 | 10 | 98.901 | #4 | 10 | 66 | #6 | 0.945 | 3224.4742 | 40 | 55 | 20 | 133.056 | 1.4784 | 0.7392 | 800 | 34 | 48 | 28 | 47.9444 | 2325.5159
60 | 2.45 | 147 | 75 | 480 | 43.75 | 12 | 182.7504 | 35 | 112.3875 | 21 | 35 | 59.0625 | 60 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 50.3125 | #8 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 1.2 | 4094.5704 | 40 | 55 | 20 | 168.96 | 1.8773 | 0.93867 | 800 | 34 | 48 | 28 | 47.9444 | 3195.6121
60 | 2.45 | 147 | 100 | 480 | 58.3333 | 12 | 182.7504 | 35 | 149.85 | 28 | 35 | 78.75 | 80 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 67.0833 | #6 | 10 | 164.835 | #1 | 10 | 110 | #3 | 1.6 | 5459.4272 | 40 | 55 | 20 | 225.28 | 2.5031 | 1.2516 | 800 | 34 | 48 | 28 | 47.9444 | 4560.4689
60 | 2.45 | 147 | 125 | 480 | 72.9167 | 12 | 182.7504 | 35 | 187.3125 | 35 | 35 | 98.4375 | 100 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 83.8542 | #4 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 2 | 6824.284 | 40 | 55 | 20 | 281.6 | 3.1289 | 1.5644 | 800 | 34 | 48 | 28 | 47.9444 | 5925.3257
60 | 2.45 | 147 | 150 | 480 | 87.5 | 12 | 182.7504 | 35 | 224.775 | 42 | 35 | 118.125 | 125 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 100.625 | #4 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 2.4 | 8189.1408 | 40 | 55 | 20 | 337.92 | 3.7547 | 1.8773 | 800 | 34 | 48 | 28 | 47.9444 | 7290.1825
60 | 2.45 | 147 | 175 | 480 | 100 | 12 | 182.7504 | 35 | 262.2375 | 48 | 35 | 135 | 150 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 115 | #3 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 2.75 | 9383.3905 | 40 | 55 | 20 | 387.2 | 4.3022 | 2.1511 | 1200 | 38 | 70 | 28 | 71.5556 | 8041.7238
60 | 2.45 | 147 | 200 | 480 | 114.5833 | 12 | 182.7504 | 35 | 299.7 | 55 | 35 | 154.6875 | 175 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 131.7708 | #2 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 3.15 | 10748.2473 | 40 | 55 | 20 | 443.52 | 4.928 | 2.464 | 1200 | 38 | 70 | 28 | 71.5556 | 9406.5806
60 | 2.45 | 147 | 250 | 480 | 143.75 | 12 | 182.7504 | 35 | 374.625 | 69 | 35 | 194.0625 | 200 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 165.3125 | #1 | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 3.95 | 13477.9609 | 40 | 55 | 20 | 556.16 | 6.1796 | 3.0898 | 1200 | 38 | 70 | 28 | 71.5556 | 12136.2942
60 | 2.45 | 147 | 300 | 480 | 172.9167 | 12 | 182.7504 | 35 | 449.55 | 83 | 35 | 233.4375 | 250 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 198.8542 | #2/0 | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 4.75 | 16207.6745 | 40 | 55 | 20 | 668.8 | 7.4311 | 3.7156 | 1200 | 38 | 70 | 28 | 71.5556 | 14866.0078
60 | 2.45 | 147 | 350 | 480 | 200 | 12 | 182.7504 | 35 | 524.475 | 96 | 35 | 270 | 300 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 230 | #3/0 | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 5.5 | 18766.781 | 40 | 55 | 20 | 774.4 | 8.6044 | 4.3022 | 1200 | 38 | 70 | 28 | 71.5556 | 17425.1143
60 | 2.45 | 147 | 400 | 480 | 229.1667 | 12 | 182.7504 | 35 | 599.4 | 110 | 35 | 309.375 | 350 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 263.5417 | #4/0 | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 6.3 | 21496.4946 | 40 | 55 | 20 | 887.04 | 9.856 | 4.928 | 1200 | 38 | 70 | 28 | 71.5556 | 20154.8279
60 | 2.45 | 147 | 450 | 480 | 258.3333 | 12 | 182.7504 | 35 | 674.325 | 124 | 35 | 348.75 | 350 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 297.0833 | #4/0 | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 7.1 | 24226.2082 | 40 | 55 | 20 | 999.68 | 11.1076 | 5.5538 | 1200 | 38 | 70 | 28 | 71.5556 | 22884.5415
60 | 2.45 | 147 | 500 | 480 | 285.4167 | 12 | 182.7504 | 35 | 749.25 | 137 | 35 | 385.3125 | 400 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 328.2292 | 250MCM | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 7.85 | 26785.3147 | 40 | 55 | 20 | 1105.28 | 12.2809 | 6.1404 | 1200 | 38 | 70 | 28 | 71.5556 | 25443.648
60 | 2.45 | 147 | 600 | 480 | 343.75 | 12 | 182.7504 | 35 | 899.1 | 165 | 35 | 464.0625 | 500 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 395.3125 | #2/0 2x | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 9.45 | 32244.7419 | 40 | 55 | 20 | 1330.56 | 14.784 | 7.392 | 1200 | 38 | 70 | 28 | 71.5556 | 30903.0752
60 | 2.45 | 147 | 700 | 480 | 400 | 12 | 182.7504 | 35 | 1048.95 | 192 | 35 | 540 | 600 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 460 | #3/0 2x | 10 | 1153.845 | Buss | 10 | 770 | Buss | 11 | 37533.562 | 40 | 55 | 20 | 1548.8 | 17.2089 | 8.6044 | 1200 | 38 | 70 | 28 | 71.5556 | 36191.8953
60 | 2.45 | 147 | 800 | 480 | 458.3333 | 12 | 182.7504 | 35 | 1198.8 | 220 | 35 | 618.75 | 700 | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 527.0833 | #4/0 2x | 10 | 1318.68 | Buss | 10 | 880 | Buss | 12.6 | 42992.9892 | 40 | 55 | 20 | 1774.08 | 19.712 | 9.856 | 1200 | 38 | 70 | 28 | 71.5556 | 41651.3225
60 | 2.45 | 147 | 900 | 480 | 514.5833 | 12 | 182.7504 | 35 | 1348.65 | 247 | 35 | 694.6875 | 700 | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 591.7708 | 250MCM 2x | 10 | 1483.515 | Buss | 10 | 990 | Buss | 14.15 | 48281.8093 | 40 | 55 | 20 | 1992.32 | 22.1369 | 11.0684 | 1200 | 38 | 70 | 28 | 71.5556 | 46940.1426
60 | 2.45 | 147 | 1000 | 480 | 570.8333 | 12 | 182.7504 | 35 | 1498.5 | 274 | 35 | 770.625 | 800 | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 656.4583 | 300MCM 2x | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 15.7 | 53570.6294 | 40 | 55 | 20 | 2210.56 | 24.5618 | 12.2809 | 1200 | 38 | 70 | 28 | 71.5556 | 52228.9627
60 | 2.45 | 147 | 1100 | 480 | 629.1667 | 12 | 182.7504 | 35 | 1648.35 | 302 | 35 | 849.375 | 900 | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 723.5417 | Buss | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 17.3 | 59030.0566 | 40 | 55 | 20 | 2435.84 | 27.0649 | 13.5324 | 1200 | 38 | 70 | 28 | 71.5556 | 57688.3899
60 | 2.45 | 147 | 1200 | 480 | 685.4167 | 12 | 182.7504 | 35 | 1798.2 | 329 | 35 | 925.3125 | 1000 | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 788.2292 | Buss | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 18.85 | 64318.8767 | 40 | 55 | 20 | 2654.08 | 29.4898 | 14.7449 | 1200 | 38 | 70 | 28 | 71.5556 | 62977.21
Specs: | [6 empty] | Transformer Sizing (1Phase) | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
240 | Vpc | Vdc max. | Idc | Vpri | Ipri | 12 | Vsec | 35 | Isec | Psec | 35 | Amps | CB1 | 30 | Amps | CB | 30 | Amps | CB | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 45 | 55 | 20 | Required | 90 | 180 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | Line Fluct % | (Vac) | Safety % | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
120 | 2.45 | 294 | 5 | 120 | 22.9167 | 12 | 365.5008 | 35 | 7.4925 | 2.75 | 35 | 30.9375 | 40 | 30 | 9.7403 | 10 | 30 | 6.5 | 10 | 15 | 26.3542 | #10 | 10 | 8.2418 | #10 | 10 | 5.5 | #10 | 0.1475 | 503.2909 | 45 | 55 | 20 | 31.152 | 0.34613 | 0.17307 | 450 | 24 | 30 | 16 | 19.3333 | 261.6243
120 | 2.45 | 294 | 10 | 208 | 26.4423 | 12 | 365.5008 | 35 | 14.985 | 5.5 | 35 | 35.6971 | 40 | 30 | 19.4805 | 20 | 30 | 13 | 15 | 15 | 30.4087 | #10 | 10 | 16.4835 | #10 | 10 | 11 | #10 | 0.295 | 1006.5819 | 45 | 55 | 20 | 62.304 | 0.69227 | 0.34613 | 450 | 24 | 30 | 16 | 19.3333 | 764.9152
120 | 2.45 | 294 | 15 | 208 | 39.6635 | 12 | 365.5008 | 35 | 22.4775 | 8.25 | 35 | 53.5457 | 60 | 30 | 29.2208 | 30 | 30 | 19.5 | 20 | 15 | 45.613 | #8 | 10 | 24.7253 | #10 | 10 | 16.5 | #10 | 0.4425 | 1509.8728 | 45 | 55 | 20 | 93.456 | 1.0384 | 0.5192 | 600 | 24 | 48 | 16 | 29.3333 | 1143.2062
120 | 2.45 | 294 | 20 | 480 | 22.9167 | 12 | 365.5008 | 35 | 29.97 | 11 | 35 | 30.9375 | 40 | 30 | 38.961 | 40 | 30 | 26 | 30 | 15 | 26.3542 | #10 | 10 | 32.967 | #10 | 10 | 22 | #10 | 0.59 | 2013.1638 | 45 | 55 | 20 | 124.608 | 1.3845 | 0.69227 | 600 | 24 | 48 | 16 | 29.3333 | 1646.4971
120 | 2.45 | 294 | 25 | 480 | 29.1667 | 12 | 365.5008 | 35 | 37.4625 | 14 | 35 | 39.375 | 40 | 30 | 48.7013 | 50 | 30 | 32.5 | 40 | 15 | 33.5417 | #10 | 10 | 41.2088 | #8 | 10 | 27.5 | #10 | 0.75 | 2559.1065 | 45 | 55 | 20 | 158.4 | 1.76 | 0.88 | 600 | 24 | 48 | 16 | 29.3333 | 2192.4398
120 | 2.45 | 294 | 30 | 480 | 34.375 | 12 | 365.5008 | 35 | 44.955 | 16.5 | 35 | 46.4062 | 50 | 30 | 58.4415 | 60 | 30 | 39 | 40 | 15 | 39.5312 | #10 | 10 | 49.4505 | #8 | 10 | 33 | #10 | 0.885 | 3019.7457 | 45 | 55 | 20 | 186.912 | 2.0768 | 1.0384 | 600 | 24 | 48 | 16 | 29.3333 | 2653.079
120 | 2.45 | 294 | 35 | 480 | 40.625 | 12 | 365.5008 | 35 | 52.4475 | 19.5 | 35 | 54.8438 | 60 | 30 | 68.1818 | 70 | 30 | 45.5 | 50 | 15 | 46.7187 | #8 | 10 | 57.6923 | #8 | 10 | 38.5 | #10 | 1.045 | 3565.6884 | 45 | 55 | 20 | 220.704 | 2.4523 | 1.2261 | 600 | 24 | 48 | 16 | 29.3333 | 3199.0217
120 | 2.45 | 294 | 40 | 480 | 45.8333 | 12 | 365.5008 | 35 | 59.94 | 22 | 35 | 61.875 | 60 | 30 | 77.922 | 80 | 30 | 52 | 60 | 15 | 52.7083 | #8 | 10 | 65.934 | #6 | 10 | 44 | #8 | 1.18 | 4026.3276 | 45 | 55 | 20 | 249.216 | 2.7691 | 1.3845 | 600 | 24 | 48 | 16 | 29.3333 | 3659.6609
120 | 2.45 | 294 | 50 | 480 | 58.3333 | 12 | 365.5008 | 35 | 74.925 | 28 | 35 | 78.75 | 80 | 30 | 97.4025 | 100 | 30 | 65 | 70 | 15 | 67.0833 | #6 | 10 | 82.4175 | #4 | 10 | 55 | #8 | 1.5 | 5118.213 | 45 | 55 | 20 | 316.8 | 3.52 | 1.76 | 800 | 34 | 48 | 28 | 47.9444 | 4518.9074
120 | 2.45 | 294 | 60 | 480 | 68.75 | 12 | 365.5008 | 35 | 89.91 | 33 | 35 | 92.8125 | 100 | 30 | 116.883 | 125 | 30 | 78 | 80 | 15 | 79.0625 | #6 | 10 | 98.901 | #4 | 10 | 66 | #6 | 1.77 | 6039.4913 | 45 | 55 | 20 | 373.824 | 4.1536 | 2.0768 | 800 | 34 | 48 | 28 | 47.9444 | 5440.1858
120 | 2.45 | 294 | 75 | 480 | 87.5 | 12 | 365.5008 | 35 | 112.3875 | 42 | 35 | 118.125 | 125 | 30 | 146.1038 | 150 | 30 | 97.5 | 100 | 15 | 100.625 | #4 | 10 | 123.6263 | #2 | 10 | 82.5 | #4 | 2.25 | 7677.3195 | 45 | 55 | 20 | 475.2 | 5.28 | 2.64 | 800 | 34 | 48 | 28 | 47.9444 | 7078.0139
120 | 2.45 | 294 | 100 | 480 | 114.5833 | 12 | 365.5008 | 35 | 149.85 | 55 | 35 | 154.6875 | 175 | 30 | 194.805 | 200 | 30 | 130 | 150 | 15 | 131.7708 | #2 | 10 | 164.835 | #1 | 10 | 110 | #3 | 2.95 | 10065.8189 | 45 | 55 | 20 | 623.04 | 6.9227 | 3.4613 | 800 | 34 | 48 | 28 | 47.9444 | 9466.5133
120 | 2.45 | 294 | 125 | 480 | 143.75 | 12 | 365.5008 | 35 | 187.3125 | 69 | 35 | 194.0625 | 200 | 30 | 243.5063 | 250 | 30 | 162.5 | 175 | 15 | 165.3125 | #1 | 10 | 206.0438 | #2/0 | 10 | 137.5 | #2 | 3.7 | 12624.9254 | 45 | 55 | 20 | 781.44 | 8.6827 | 4.3413 | 800 | 34 | 48 | 28 | 47.9444 | 12025.6198
120 | 2.45 | 294 | 150 | 480 | 172.9167 | 12 | 365.5008 | 35 | 224.775 | 83 | 35 | 233.4375 | 250 | 30 | 292.2075 | 300 | 30 | 195 | 200 | 15 | 198.8542 | #2/0 | 10 | 247.2525 | #3/0 | 10 | 165 | #1 | 4.45 | 15184.0319 | 45 | 55 | 20 | 939.84 | 10.4427 | 5.2213 | 800 | 34 | 48 | 28 | 47.9444 | 14584.7263
120 | 2.45 | 294 | 175 | 480 | 200 | 12 | 365.5008 | 35 | 262.2375 | 96 | 35 | 270 | 300 | 30 | 340.9088 | 350 | 30 | 227.5 | 250 | 15 | 230 | #3/0 | 10 | 288.4613 | #4/0 | 10 | 192.5 | #1/0 | 5.15 | 17572.5313 | 45 | 55 | 20 | 1087.68 | 12.0853 | 6.0427 | 1200 | 38 | 70 | 28 | 71.5556 | 16678.0869
120 | 2.45 | 294 | 200 | 480 | 229.1667 | 12 | 365.5008 | 35 | 299.7 | 110 | 35 | 309.375 | 350 | 30 | 389.61 | 400 | 30 | 260 | 300 | 15 | 263.5417 | #4/0 | 10 | 329.67 | 250MCM | 10 | 220 | #2/0 | 5.9 | 20131.6378 | 45 | 55 | 20 | 1246.08 | 13.8453 | 6.9227 | 1200 | 38 | 70 | 28 | 71.5556 | 19237.1934
120 | 2.45 | 294 | 250 | 480 | 285.4167 | 12 | 365.5008 | 35 | 374.625 | 137 | 35 | 385.3125 | 400 | 30 | 487.0125 | 500 | 30 | 325 | 350 | 15 | 328.2292 | 250MCM | 10 | 412.0875 | #2/0 2x | 10 | 275 | #4/0 | 7.35 | 25079.2437 | 45 | 55 | 20 | 1552.32 | 17.248 | 8.624 | 1200 | 38 | 70 | 28 | 71.5556 | 24184.7993
120 | 2.45 | 294 | 300 | 480 | 343.75 | 12 | 365.5008 | 35 | 449.55 | 165 | 35 | 464.0625 | 500 | 30 | 584.415 | 600 | 30 | 390 | 400 | 15 | 395.3125 | #2/0 2x | 10 | 494.505 | #3/0 2x | 10 | 330 | 250MCM | 8.85 | 30197.4567 | 45 | 55 | 20 | 1869.12 | 20.768 | 10.384 | 1200 | 38 | 70 | 28 | 71.5556 | 29303.0123
120 | 2.45 | 294 | 350 | 480 | 400 | 12 | 365.5008 | 35 | 524.475 | 192 | 35 | 540 | 600 | 30 | 681.8175 | 700 | 30 | 455 | 500 | 15 | 460 | #3/0 2x | 10 | 576.9225 | #4/0 2x | 10 | 385 | #2/0 2x | 10.3 | 35145.0626 | 45 | 55 | 20 | 2175.36 | 24.1707 | 12.0853 | 1200 | 38 | 70 | 28 | 71.5556 | 34250.6182
120 | 2.45 | 294 | 400 | 480 | 458.3333 | 12 | 365.5008 | 35 | 599.4 | 220 | 35 | 618.75 | 700 | 30 | 779.22 | 800 | 30 | 520 | 600 | 15 | 527.0833 | #4/0 2x | 10 | 659.34 | 300MCM 2x | 10 | 440 | #3/0 2x | 11.8 | 40263.2756 | 45 | 55 | 20 | 2492.16 | 27.6907 | 13.8453 | 1200 | 38 | 70 | 28 | 71.5556 | 39368.8312
120 | 2.45 | 294 | 450 | 480 | 514.5833 | 12 | 365.5008 | 35 | 674.325 | 247 | 35 | 694.6875 | 700 | 30 | 876.6225 | 900 | 30 | 585 | 600 | 15 | 591.7708 | 250MCM 2x | 10 | 741.7575 | Buss | 10 | 495 | #3/0 2x | 13.25 | 45210.8815 | 45 | 55 | 20 | 2798.4 | 31.0933 | 15.5467 | 1200 | 38 | 70 | 28 | 71.5556 | 44316.4371
120 | 2.45 | 294 | 500 | 480 | 570.8333 | 12 | 365.5008 | 35 | 749.25 | 274 | 35 | 770.625 | 800 | 30 | 974.025 | 1000 | 30 | 650 | 700 | 15 | 656.4583 | 300MCM 2x | 10 | 824.175 | Buss | 10 | 550 | #4/0 2x | 14.7 | 50158.4874 | 45 | 55 | 20 | 3104.64 | 34.496 | 17.248 | 1200 | 38 | 70 | 28 | 71.5556 | 49264.043
120 | 2.45 | 294 | 600 | 480 | 685.4167 | 12 | 365.5008 | 35 | 899.1 | 329 | 35 | 925.3125 | 1000 | 30 | 1168.83 | 1200 | 30 | 780 | 800 | 15 | 788.2292 | Buss | 10 | 989.01 | Buss | 10 | 660 | 300MCM 2x | 17.65 | 60224.3063 | 45 | 55 | 20 | 3727.68 | 41.4187 | 20.7093 | 1200 | 38 | 70 | 28 | 71.5556 | 59329.8619
120 | 2.45 | 294 | 700 | 480 | 800 | 12 | 365.5008 | 35 | 1048.95 | 384 | 35 | 1080 | 1200 | 30 | 1363.635 | Check | 30 | 910 | 1000 | 15 | 920 | Buss | 10 | 1153.845 | Buss | 10 | 770 | Buss | 20.6 | 70290.1252 | 45 | 55 | 20 | 4350.72 | 48.3413 | 24.1707 | 1200 | 38 | 70 | 28 | 71.5556 | 69395.6808
120 | 2.45 | 294 | 800 | 480 | 914.5833 | 12 | 365.5008 | 35 | 1198.8 | 439 | 35 | 1234.6875 | Check | 30 | 1558.44 | Check | 30 | 1040 | 1200 | 15 | 1051.7708 | Buss | 10 | 1318.68 | Buss | 10 | 880 | Buss | 23.55 | 80355.9441 | 45 | 55 | 20 | 4973.76 | 55.264 | 27.632 | 1200 | 38 | 70 | 28 | 71.5556 | 79461.4997
120 | 2.45 | 294 | 900 | 480 | 1027.0833 | 12 | 365.5008 | 35 | 1348.65 | 493 | 35 | 1386.5625 | Check | 30 | 1753.245 | Check | 30 | 1170 | 1200 | 15 | 1181.1458 | Buss | 10 | 1483.515 | Buss | 10 | 990 | Buss | 26.45 | 90251.1559 | 45 | 55 | 20 | 5586.24 | 62.0693 | 31.0347 | 1200 | 38 | 70 | 28 | 71.5556 | 89356.7115
120 | 2.45 | 294 | 1000 | 480 | 1141.6667 | 12 | 365.5008 | 35 | 1498.5 | 548 | 35 | 1541.25 | Check | 30 | 1948.05 | Check | 30 | 1300 | Check | 15 | 1312.9167 | Buss | 10 | 1648.35 | Buss | 10 | 1100 | Buss | 29.4 | 100316.9748 | 45 | 55 | 20 | 6209.28 | 68.992 | 34.496 | 1200 | 38 | 70 | 28 | 71.5556 | 99422.5304
120 | 2.45 | 294 | 1100 | 480 | 1256.25 | 12 | 365.5008 | 35 | 1648.35 | 603 | 35 | 1695.9375 | Check | 30 | 2142.855 | Check | 30 | 1430 | Check | 15 | 1444.6875 | Buss | 10 | 1813.185 | Buss | 10 | 1210 | Buss | 32.35 | 110382.7937 | 45 | 55 | 20 | 6832.32 | 75.9147 | 37.9573 | 1200 | 38 | 70 | 28 | 71.5556 | 109488.3493
120 | 2.45 | 294 | 1200 | 480 | 1370.8333 | 12 | 365.5008 | 35 | 1798.2 | 658 | 35 | 1850.625 | Check | 30 | 2337.66 | Check | 30 | 1560 | Check | 15 | 1576.4583 | Buss | 10 | 1978.02 | Buss | 10 | 1320 | Buss | 35.3 | 120448.6126 | 45 | 55 | 20 | 7455.36 | 82.8373 | 41.4187 | 1200 | 38 | 70 | 28 | 71.5556 | 119554.1682

## 3PH Battery Chargers
3 PHASE Battery Chargers | [5 empty] | VERIFIER LES COEFFICIENT DES TRANSFOS AVEC DES MODELES EXISTANTS
Vnom | Idc | #cel | VPC | Vmax | Vsec | Isec | Psec |  | P | Iprim | At Vac | CB1 | AWG | AWG | AWG | CB2 | SCR | VM | AM | fuse
(Vdc) | (Idc) |  | (Vdc) | (Vdc) | (Vac) | (Iac) | (Kva) |  | (Kva) | (Iac) | (Vac) | (Iac) | Prim | Sec | DC | (Idc) | Model | Scale | Scale | (A)
Specs: | [6 empty] | Transformer Sizing (3 Phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
380 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % |  | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
190 | 1.65 | 313.5 | 5 | 120 | 10.8253 | 12 | 150.2794 | 260.2915 | 20 | 4.98 | 2.25 | 30 | 14.0729 | 15 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 12.4491 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.1675 | 571.5338 | 40 | 55 | 20 | 23.584 | 0.23584 | 0.11792 | 450 | 24 | 30 | 16 | 19.3333 | 209.0338
190 | 2.15 | 408.5 | 108 | 120 | 307.9201 | 12 | 195.8186 | 339.1677 | 20 | 107.568 | 64 | 30 | 400.2962 | 400 | 30 | 139.8384 | 150 | 30 | 140.4 | 150 | 15 | 354.1082 | 300MCM | 10 | 118.3248 | #3 | 10 | 118.8 | #3 | 4.696 | 16023.4188 | 40 | 55 | 20 | 661.1968 | 6.612 | 3.306 | 450 | 24 | 30 | 16 | 19.3333 | 15660.9188
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
12 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
6 | 2.45 | 14.7 | 5 | 120 | 1.2028 | 12 | 10.0466 | 17.4012 | 20 | 4.98 | 0.25 | 30 | 1.5637 | 5 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 1.3832 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.0275 | 93.8339 | 40 | 55 | 20 | 3.872 | 0.03872 | 0.01936 | 450 | 24 | 30 | 16 | 19.3333 | -268.6661
6 | 2.45 | 14.7 | 10 | 120 | 2.4056 | 12 | 10.0466 | 17.4012 | 20 | 9.96 | 0.5 | 30 | 3.1273 | 5 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 2.7665 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.055 | 187.6678 | 40 | 55 | 20 | 7.744 | 0.07744 | 0.03872 | 450 | 24 | 30 | 16 | 19.3333 | -174.8322
6 | 2.45 | 14.7 | 15 | 120 | 2.4056 | 12 | 10.0466 | 17.4012 | 20 | 14.94 | 0.5 | 30 | 3.1273 | 5 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 2.7665 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.065 | 221.7892 | 40 | 55 | 20 | 9.152 | 0.09152 | 0.04576 | 600 | 24 | 48 | 16 | 29.3333 | -328.2108
6 | 2.45 | 14.7 | 20 | 120 | 3.6084 | 12 | 10.0466 | 17.4012 | 20 | 19.92 | 0.75 | 30 | 4.691 | 5 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 4.1497 | #10 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.0925 | 315.6231 | 40 | 55 | 20 | 13.024 | 0.13024 | 0.06512 | 600 | 24 | 48 | 16 | 29.3333 | -234.3769
6 | 2.45 | 14.7 | 25 | 120 | 4.8113 | 12 | 10.0466 | 17.4012 | 20 | 24.9 | 1 | 30 | 6.2546 | 10 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 5.5329 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.12 | 409.457 | 40 | 55 | 20 | 16.896 | 0.16896 | 0.08448 | 600 | 24 | 48 | 16 | 29.3333 | -140.543
6 | 2.45 | 14.7 | 30 | 120 | 4.8113 | 12 | 10.0466 | 17.4012 | 20 | 29.88 | 1 | 30 | 6.2546 | 10 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 5.5329 | #10 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.13 | 443.5785 | 40 | 55 | 20 | 18.304 | 0.18304 | 0.09152 | 600 | 24 | 48 | 16 | 29.3333 | -106.4215
6 | 2.45 | 14.7 | 35 | 120 | 6.0141 | 12 | 10.0466 | 17.4012 | 20 | 34.86 | 1.25 | 30 | 7.8183 | 10 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 6.9162 | #10 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 0.1575 | 537.4124 | 40 | 55 | 20 | 22.176 | 0.22176 | 0.11088 | 600 | 24 | 48 | 16 | 29.3333 | -12.5876
6 | 2.45 | 14.7 | 40 | 120 | 6.0141 | 12 | 10.0466 | 17.4012 | 20 | 39.84 | 1.25 | 30 | 7.8183 | 10 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 6.9162 | #10 | 10 | 43.824 | #8 | 10 | 44 | #8 | 0.1675 | 571.5338 | 40 | 55 | 20 | 23.584 | 0.23584 | 0.11792 | 600 | 24 | 48 | 16 | 29.3333 | 21.5338
6 | 2.45 | 14.7 | 50 | 120 | 8.4197 | 12 | 10.0466 | 17.4012 | 20 | 49.8 | 1.75 | 30 | 10.9456 | 15 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 9.6826 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 0.2225 | 759.2016 | 40 | 55 | 20 | 31.328 | 0.31328 | 0.15664 | 800 | 34 | 48 | 28 | 47.9444 | -139.7567
6 | 2.45 | 14.7 | 60 | 120 | 9.6225 | 12 | 10.0466 | 17.4012 | 20 | 59.76 | 2 | 30 | 12.5093 | 15 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 11.0659 | #10 | 10 | 65.736 | #6 | 10 | 66 | #6 | 0.26 | 887.1569 | 40 | 55 | 20 | 36.608 | 0.36608 | 0.18304 | 800 | 34 | 48 | 28 | 47.9444 | -11.8014
6 | 2.45 | 14.7 | 75 | 120 | 12.0281 | 12 | 10.0466 | 17.4012 | 20 | 74.7 | 2.5 | 30 | 15.6366 | 20 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 13.8324 | #10 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 0.325 | 1108.9461 | 40 | 55 | 20 | 45.76 | 0.4576 | 0.2288 | 800 | 34 | 48 | 28 | 47.9444 | 209.9878
6 | 2.45 | 14.7 | 100 | 120 | 15.6366 | 12 | 10.0466 | 17.4012 | 20 | 99.6 | 3.25 | 30 | 20.3275 | 25 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 17.9821 | #10 | 10 | 109.56 | #3 | 10 | 110 | #3 | 0.4275 | 1458.6907 | 40 | 55 | 20 | 60.192 | 0.60192 | 0.30096 | 800 | 34 | 48 | 28 | 47.9444 | 559.7324
6 | 2.45 | 14.7 | 125 | 120 | 19.245 | 12 | 10.0466 | 17.4012 | 20 | 124.5 | 4 | 30 | 25.0185 | 25 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 22.1318 | #10 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 0.53 | 1808.4353 | 40 | 55 | 20 | 74.624 | 0.74624 | 0.37312 | 800 | 34 | 48 | 28 | 47.9444 | 909.4769
6 | 2.45 | 14.7 | 150 | 120 | 22.8534 | 12 | 10.0466 | 17.4012 | 20 | 149.4 | 4.75 | 30 | 29.7095 | 30 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 26.2815 | #10 | 10 | 164.34 | #1 | 10 | 165 | #1 | 0.6325 | 2158.1798 | 40 | 55 | 20 | 89.056 | 0.89056 | 0.44528 | 800 | 34 | 48 | 28 | 47.9444 | 1259.2215
6 | 2.45 | 14.7 | 175 | 120 | 26.4619 | 12 | 10.0466 | 17.4012 | 20 | 174.3 | 5.5 | 30 | 34.4005 | 40 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 30.4312 | #10 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 0.735 | 2507.9244 | 40 | 55 | 20 | 103.488 | 1.0349 | 0.51744 | 1200 | 38 | 70 | 28 | 71.5556 | 1166.2577
6 | 2.45 | 14.7 | 200 | 120 | 30.0703 | 12 | 10.0466 | 17.4012 | 20 | 199.2 | 6.25 | 30 | 39.0914 | 40 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 34.5809 | #10 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 0.8375 | 2857.6689 | 40 | 55 | 20 | 117.92 | 1.1792 | 0.5896 | 1200 | 38 | 70 | 28 | 71.5556 | 1516.0023
6 | 2.45 | 14.7 | 250 | 120 | 37.2872 | 12 | 10.0466 | 17.4012 | 20 | 249 | 7.75 | 30 | 48.4734 | 50 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 42.8803 | #8 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 1.0425 | 3557.158 | 40 | 55 | 20 | 146.784 | 1.4678 | 0.73392 | 1200 | 38 | 70 | 28 | 71.5556 | 2215.4914
6 | 2.45 | 14.7 | 300 | 208 | 25.6754 | 12 | 10.0466 | 17.4012 | 20 | 298.8 | 9.25 | 30 | 33.3781 | 40 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 29.5267 | #10 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 1.2475 | 4256.6471 | 40 | 55 | 20 | 175.648 | 1.7565 | 0.87824 | 1200 | 38 | 70 | 28 | 71.5556 | 2914.9805
6 | 2.45 | 14.7 | 350 | 208 | 30.5329 | 12 | 10.0466 | 17.4012 | 20 | 348.6 | 11 | 30 | 39.6928 | 40 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 35.1129 | #10 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 1.47 | 5015.8487 | 40 | 55 | 20 | 206.976 | 2.0698 | 1.0349 | 1200 | 38 | 70 | 28 | 71.5556 | 3674.1821
6 | 2.45 | 14.7 | 400 | 208 | 34.6965 | 12 | 10.0466 | 17.4012 | 20 | 398.4 | 12.5 | 30 | 45.1055 | 50 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 39.901 | #10 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 1.675 | 5715.3378 | 40 | 55 | 20 | 235.84 | 2.3584 | 1.1792 | 1200 | 38 | 70 | 28 | 71.5556 | 4373.6712
6 | 2.45 | 14.7 | 450 | 208 | 38.8601 | 12 | 10.0466 | 17.4012 | 20 | 448.2 | 14 | 30 | 50.5181 | 60 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 44.6891 | #8 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 1.88 | 6414.827 | 40 | 55 | 20 | 264.704 | 2.647 | 1.3235 | 1200 | 38 | 70 | 28 | 71.5556 | 5073.1603
6 | 2.45 | 14.7 | 500 | 208 | 43.0237 | 12 | 10.0466 | 17.4012 | 20 | 498 | 15.5 | 30 | 55.9308 | 60 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 49.4773 | #8 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 2.085 | 7114.3161 | 40 | 55 | 20 | 293.568 | 2.9357 | 1.4678 | 1200 | 38 | 70 | 28 | 71.5556 | 5772.6494
6 | 2.45 | 14.7 | 600 | 480 | 22.252 | 12 | 10.0466 | 17.4012 | 20 | 597.6 | 18.5 | 30 | 28.9277 | 30 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 25.5898 | #10 | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 2.495 | 8513.2943 | 40 | 55 | 20 | 351.296 | 3.513 | 1.7565 | 1200 | 38 | 70 | 28 | 71.5556 | 7171.6276
6 | 2.45 | 14.7 | 700 | 480 | 26.4619 | 12 | 10.0466 | 17.4012 | 20 | 697.2 | 22 | 30 | 34.4005 | 40 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 30.4312 | #10 | 10 | 766.92 | Buss | 10 | 770 | Buss | 2.94 | 10031.6975 | 40 | 55 | 20 | 413.952 | 4.1395 | 2.0698 | 1200 | 38 | 70 | 28 | 71.5556 | 8690.0308
6 | 2.45 | 14.7 | 800 | 480 | 30.0703 | 12 | 10.0466 | 17.4012 | 20 | 796.8 | 25 | 30 | 39.0914 | 40 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 34.5809 | #10 | 10 | 876.48 | Buss | 10 | 880 | Buss | 3.35 | 11430.6757 | 40 | 55 | 20 | 471.68 | 4.7168 | 2.3584 | 1200 | 38 | 70 | 28 | 71.5556 | 10089.009
6 | 2.45 | 14.7 | 900 | 480 | 33.6788 | 12 | 10.0466 | 17.4012 | 20 | 896.4 | 28 | 30 | 43.7824 | 50 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 38.7306 | #10 | 10 | 986.04 | Buss | 10 | 990 | Buss | 3.76 | 12829.6539 | 40 | 55 | 20 | 529.408 | 5.2941 | 2.647 | 1200 | 38 | 70 | 28 | 71.5556 | 11487.9873
6 | 2.45 | 14.7 | 1000 | 480 | 37.2872 | 12 | 10.0466 | 17.4012 | 20 | 996 | 31 | 30 | 48.4734 | 50 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 42.8803 | #8 | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 4.17 | 14228.6321 | 40 | 55 | 20 | 587.136 | 5.8714 | 2.9357 | 1200 | 38 | 70 | 28 | 71.5556 | 12886.9655
6 | 2.45 | 14.7 | 1100 | 480 | 40.8956 | 12 | 10.0466 | 17.4012 | 20 | 1095.6 | 34 | 30 | 53.1643 | 60 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 47.03 | #8 | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 4.58 | 15627.6104 | 40 | 55 | 20 | 644.864 | 6.4486 | 3.2243 | 1200 | 38 | 70 | 28 | 71.5556 | 14285.9437
6 | 2.45 | 14.7 | 1200 | 480 | 44.5041 | 12 | 10.0466 | 17.4012 | 20 | 1195.2 | 37 | 30 | 57.8553 | 60 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 51.1797 | #8 | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 4.99 | 17026.5886 | 40 | 55 | 20 | 702.592 | 7.0259 | 3.513 | 1200 | 38 | 70 | 28 | 71.5556 | 15684.9219
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
24 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
12 | 2.45 | 29.4 | 5 | 120 | 2.4056 | 12 | 17.0932 | 29.6063 | 20 | 4.98 | 0.5 | 30 | 3.1273 | 5 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 2.7665 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.045 | 153.5464 | 40 | 55 | 20 | 6.336 | 0.06336 | 0.03168 | 450 | 24 | 30 | 16 | 19.3333 | -208.9536
12 | 2.45 | 29.4 | 10 | 120 | 3.6084 | 12 | 17.0932 | 29.6063 | 20 | 9.96 | 0.75 | 30 | 4.691 | 5 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 4.1497 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.0725 | 247.3803 | 40 | 55 | 20 | 10.208 | 0.10208 | 0.05104 | 450 | 24 | 30 | 16 | 19.3333 | -115.1197
12 | 2.45 | 29.4 | 15 | 120 | 4.8113 | 12 | 17.0932 | 29.6063 | 20 | 14.94 | 1 | 30 | 6.2546 | 10 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 5.5329 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.1 | 341.2142 | 40 | 55 | 20 | 14.08 | 0.1408 | 0.0704 | 600 | 24 | 48 | 16 | 29.3333 | -208.7858
12 | 2.45 | 29.4 | 20 | 120 | 6.0141 | 12 | 17.0932 | 29.6063 | 20 | 19.92 | 1.25 | 30 | 7.8183 | 10 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 6.9162 | #10 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.1275 | 435.0481 | 40 | 55 | 20 | 17.952 | 0.17952 | 0.08976 | 600 | 24 | 48 | 16 | 29.3333 | -114.9519
12 | 2.45 | 29.4 | 25 | 120 | 7.2169 | 12 | 17.0932 | 29.6063 | 20 | 24.9 | 1.5 | 30 | 9.3819 | 10 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 8.2994 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.155 | 528.882 | 40 | 55 | 20 | 21.824 | 0.21824 | 0.10912 | 600 | 24 | 48 | 16 | 29.3333 | -21.118
12 | 2.45 | 29.4 | 30 | 120 | 8.4197 | 12 | 17.0932 | 29.6063 | 20 | 29.88 | 1.75 | 30 | 10.9456 | 15 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 9.6826 | #10 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.1825 | 622.7159 | 40 | 55 | 20 | 25.696 | 0.25696 | 0.12848 | 600 | 24 | 48 | 16 | 29.3333 | 72.7159
12 | 2.45 | 29.4 | 35 | 120 | 9.6225 | 12 | 17.0932 | 29.6063 | 20 | 34.86 | 2 | 30 | 12.5093 | 15 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 11.0659 | #10 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 0.21 | 716.5498 | 40 | 55 | 20 | 29.568 | 0.29568 | 0.14784 | 600 | 24 | 48 | 16 | 29.3333 | 166.5498
12 | 2.45 | 29.4 | 40 | 120 | 10.8253 | 12 | 17.0932 | 29.6063 | 20 | 39.84 | 2.25 | 30 | 14.0729 | 15 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 12.4491 | #10 | 10 | 43.824 | #8 | 10 | 44 | #8 | 0.2375 | 810.3837 | 40 | 55 | 20 | 33.44 | 0.3344 | 0.1672 | 600 | 24 | 48 | 16 | 29.3333 | 260.3837
12 | 2.45 | 29.4 | 50 | 120 | 13.2309 | 12 | 17.0932 | 29.6063 | 20 | 49.8 | 2.75 | 30 | 17.2002 | 20 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 15.2156 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 0.2925 | 998.0515 | 40 | 55 | 20 | 41.184 | 0.41184 | 0.20592 | 800 | 34 | 48 | 28 | 47.9444 | 99.0932
12 | 2.45 | 29.4 | 60 | 120 | 15.6366 | 12 | 17.0932 | 29.6063 | 20 | 59.76 | 3.25 | 30 | 20.3275 | 25 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 17.9821 | #10 | 10 | 65.736 | #6 | 10 | 66 | #6 | 0.3475 | 1185.7193 | 40 | 55 | 20 | 48.928 | 0.48928 | 0.24464 | 800 | 34 | 48 | 28 | 47.9444 | 286.761
12 | 2.45 | 29.4 | 75 | 120 | 19.245 | 12 | 17.0932 | 29.6063 | 20 | 74.7 | 4 | 30 | 25.0185 | 25 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 22.1318 | #10 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 0.43 | 1467.2211 | 40 | 55 | 20 | 60.544 | 0.60544 | 0.30272 | 800 | 34 | 48 | 28 | 47.9444 | 568.2627
12 | 2.45 | 29.4 | 100 | 120 | 25.2591 | 12 | 17.0932 | 29.6063 | 20 | 99.6 | 5.25 | 30 | 32.8368 | 40 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 29.0479 | #10 | 10 | 109.56 | #3 | 10 | 110 | #3 | 0.5675 | 1936.3906 | 40 | 55 | 20 | 79.904 | 0.79904 | 0.39952 | 800 | 34 | 48 | 28 | 47.9444 | 1037.4323
12 | 2.45 | 29.4 | 125 | 120 | 31.2731 | 12 | 17.0932 | 29.6063 | 20 | 124.5 | 6.5 | 30 | 40.6551 | 50 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 35.9641 | #10 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 0.705 | 2405.5601 | 40 | 55 | 20 | 99.264 | 0.99264 | 0.49632 | 800 | 34 | 48 | 28 | 47.9444 | 1506.6018
12 | 2.45 | 29.4 | 150 | 480 | 9.3218 | 12 | 17.0932 | 29.6063 | 20 | 149.4 | 7.75 | 30 | 12.1183 | 15 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 10.7201 | #10 | 10 | 164.34 | #1 | 10 | 165 | #1 | 0.8425 | 2874.7296 | 40 | 55 | 20 | 118.624 | 1.1862 | 0.59312 | 800 | 34 | 48 | 28 | 47.9444 | 1975.7713
12 | 2.45 | 29.4 | 175 | 120 | 43.3013 | 12 | 17.0932 | 29.6063 | 20 | 174.3 | 9 | 30 | 56.2917 | 60 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 49.7965 | #8 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 0.98 | 3343.8992 | 40 | 55 | 20 | 137.984 | 1.3798 | 0.68992 | 1200 | 38 | 70 | 28 | 71.5556 | 2002.2325
12 | 2.45 | 29.4 | 200 | 208 | 29.1451 | 12 | 17.0932 | 29.6063 | 20 | 199.2 | 10.5 | 30 | 37.8886 | 40 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 33.5168 | #10 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 1.135 | 3872.7812 | 40 | 55 | 20 | 159.808 | 1.5981 | 0.79904 | 1200 | 38 | 70 | 28 | 71.5556 | 2531.1145
12 | 2.45 | 29.4 | 250 | 208 | 36.0844 | 12 | 17.0932 | 29.6063 | 20 | 249 | 13 | 30 | 46.9097 | 50 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 41.4971 | #8 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 1.41 | 4811.1202 | 40 | 55 | 20 | 198.528 | 1.9853 | 0.99264 | 1200 | 38 | 70 | 28 | 71.5556 | 3469.4536
12 | 2.45 | 29.4 | 300 | 208 | 43.0237 | 12 | 17.0932 | 29.6063 | 20 | 298.8 | 15.5 | 30 | 55.9308 | 60 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 49.4773 | #8 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 1.685 | 5749.4593 | 40 | 55 | 20 | 237.248 | 2.3725 | 1.1862 | 1200 | 38 | 70 | 28 | 71.5556 | 4407.7926
12 | 2.45 | 29.4 | 350 | 240 | 43.3013 | 12 | 17.0932 | 29.6063 | 20 | 348.6 | 18 | 30 | 56.2917 | 60 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 49.7965 | #8 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 1.96 | 6687.7983 | 40 | 55 | 20 | 275.968 | 2.7597 | 1.3798 | 1200 | 38 | 70 | 28 | 71.5556 | 5346.1317
12 | 2.45 | 29.4 | 400 | 480 | 25.2591 | 12 | 17.0932 | 29.6063 | 20 | 398.4 | 21 | 30 | 32.8368 | 40 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 29.0479 | #10 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 2.27 | 7745.5623 | 40 | 55 | 20 | 319.616 | 3.1962 | 1.5981 | 1200 | 38 | 70 | 28 | 71.5556 | 6403.8957
12 | 2.45 | 29.4 | 450 | 480 | 27.6647 | 12 | 17.0932 | 29.6063 | 20 | 448.2 | 23 | 30 | 35.9641 | 40 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 31.8144 | #10 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 2.51 | 8564.4764 | 40 | 55 | 20 | 353.408 | 3.5341 | 1.767 | 1200 | 38 | 70 | 28 | 71.5556 | 7222.8098
12 | 2.45 | 29.4 | 500 | 480 | 31.2731 | 12 | 17.0932 | 29.6063 | 20 | 498 | 26 | 30 | 40.6551 | 50 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 35.9641 | #10 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 2.82 | 9622.2404 | 40 | 55 | 20 | 397.056 | 3.9706 | 1.9853 | 1200 | 38 | 70 | 28 | 71.5556 | 8280.5738
12 | 2.45 | 29.4 | 600 | 480 | 37.2872 | 12 | 17.0932 | 29.6063 | 20 | 597.6 | 31 | 30 | 48.4734 | 50 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 42.8803 | #8 | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 3.37 | 11498.9185 | 40 | 55 | 20 | 474.496 | 4.745 | 2.3725 | 1200 | 38 | 70 | 28 | 71.5556 | 10157.2519
12 | 2.45 | 29.4 | 700 | 480 | 43.3013 | 12 | 17.0932 | 29.6063 | 20 | 697.2 | 36 | 30 | 56.2917 | 60 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 49.7965 | #8 | 10 | 766.92 | Buss | 10 | 770 | Buss | 3.92 | 13375.5966 | 40 | 55 | 20 | 551.936 | 5.5194 | 2.7597 | 1200 | 38 | 70 | 28 | 71.5556 | 12033.93
12 | 2.45 | 29.4 | 800 | 480 | 49.3153 | 12 | 17.0932 | 29.6063 | 20 | 796.8 | 41 | 30 | 64.1099 | 70 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 56.7126 | #8 | 10 | 876.48 | Buss | 10 | 880 | Buss | 4.47 | 15252.2747 | 40 | 55 | 20 | 629.376 | 6.2938 | 3.1469 | 1200 | 38 | 70 | 28 | 71.5556 | 13910.6081
12 | 2.45 | 29.4 | 900 | 480 | 55.3294 | 12 | 17.0932 | 29.6063 | 20 | 896.4 | 46 | 30 | 71.9282 | 80 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 63.6288 | #6 | 10 | 986.04 | Buss | 10 | 990 | Buss | 5.02 | 17128.9528 | 40 | 55 | 20 | 706.816 | 7.0682 | 3.5341 | 1200 | 38 | 70 | 28 | 71.5556 | 15787.2862
12 | 2.45 | 29.4 | 1000 | 480 | 62.5463 | 12 | 17.0932 | 29.6063 | 20 | 996 | 52 | 30 | 81.3102 | 90 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 71.9282 | #6 | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 5.64 | 19244.4809 | 40 | 55 | 20 | 794.112 | 7.9411 | 3.9706 | 1200 | 38 | 70 | 28 | 71.5556 | 17902.8142
12 | 2.45 | 29.4 | 1100 | 480 | 68.5603 | 12 | 17.0932 | 29.6063 | 20 | 1095.6 | 57 | 30 | 89.1284 | 90 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 78.8444 | #6 | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 6.19 | 21121.159 | 40 | 55 | 20 | 871.552 | 8.7155 | 4.3578 | 1200 | 38 | 70 | 28 | 71.5556 | 19779.4923
12 | 2.45 | 29.4 | 1200 | 480 | 74.5744 | 12 | 17.0932 | 29.6063 | 20 | 1195.2 | 62 | 30 | 96.9467 | 100 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 85.7606 | #4 | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 6.74 | 22997.8371 | 40 | 55 | 20 | 948.992 | 9.4899 | 4.745 | 1200 | 38 | 70 | 28 | 71.5556 | 21656.1704
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
36 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
18 | 2.45 | 44.1 | 5 | 120 | 2.4056 | 12 | 24.1398 | 41.8113 | 20 | 4.98 | 0.5 | 30 | 3.1273 | 5 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 2.7665 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.045 | 153.5464 | 40 | 55 | 20 | 6.336 | 0.06336 | 0.03168 | 450 | 24 | 30 | 16 | 19.3333 | -208.9536
18 | 2.45 | 44.1 | 10 | 120 | 3.6084 | 12 | 24.1398 | 41.8113 | 20 | 9.96 | 0.75 | 30 | 4.691 | 5 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 4.1497 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.0725 | 247.3803 | 40 | 55 | 20 | 10.208 | 0.10208 | 0.05104 | 450 | 24 | 30 | 16 | 19.3333 | -115.1197
18 | 2.45 | 44.1 | 15 | 120 | 6.0141 | 12 | 24.1398 | 41.8113 | 20 | 14.94 | 1.25 | 30 | 7.8183 | 10 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 6.9162 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.1175 | 400.9267 | 40 | 55 | 20 | 16.544 | 0.16544 | 0.08272 | 600 | 24 | 48 | 16 | 29.3333 | -149.0733
18 | 2.45 | 44.1 | 20 | 120 | 7.2169 | 12 | 24.1398 | 41.8113 | 20 | 19.92 | 1.5 | 30 | 9.3819 | 10 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 8.2994 | #10 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.145 | 494.7606 | 40 | 55 | 20 | 20.416 | 0.20416 | 0.10208 | 600 | 24 | 48 | 16 | 29.3333 | -55.2394
18 | 2.45 | 44.1 | 25 | 120 | 9.6225 | 12 | 24.1398 | 41.8113 | 20 | 24.9 | 2 | 30 | 12.5093 | 15 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 11.0659 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.19 | 648.307 | 40 | 55 | 20 | 26.752 | 0.26752 | 0.13376 | 600 | 24 | 48 | 16 | 29.3333 | 98.307
18 | 2.45 | 44.1 | 30 | 120 | 10.8253 | 12 | 24.1398 | 41.8113 | 20 | 29.88 | 2.25 | 30 | 14.0729 | 15 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 12.4491 | #10 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.2175 | 742.1409 | 40 | 55 | 20 | 30.624 | 0.30624 | 0.15312 | 600 | 24 | 48 | 16 | 29.3333 | 192.1409
18 | 2.45 | 44.1 | 35 | 120 | 13.2309 | 12 | 24.1398 | 41.8113 | 20 | 34.86 | 2.75 | 30 | 17.2002 | 20 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 15.2156 | #10 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 0.2625 | 895.6873 | 40 | 55 | 20 | 36.96 | 0.3696 | 0.1848 | 600 | 24 | 48 | 16 | 29.3333 | 345.6873
18 | 2.45 | 44.1 | 40 | 120 | 14.4338 | 12 | 24.1398 | 41.8113 | 20 | 39.84 | 3 | 30 | 18.7639 | 20 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 16.5988 | #10 | 10 | 43.824 | #8 | 10 | 44 | #8 | 0.29 | 989.5212 | 40 | 55 | 20 | 40.832 | 0.40832 | 0.20416 | 600 | 24 | 48 | 16 | 29.3333 | 439.5212
18 | 2.45 | 44.1 | 50 | 120 | 18.0422 | 12 | 24.1398 | 41.8113 | 20 | 49.8 | 3.75 | 30 | 23.4549 | 25 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 20.7485 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 0.3625 | 1236.9015 | 40 | 55 | 20 | 51.04 | 0.5104 | 0.2552 | 800 | 34 | 48 | 28 | 47.9444 | 337.9431
18 | 2.45 | 44.1 | 60 | 120 | 21.6506 | 12 | 24.1398 | 41.8113 | 20 | 59.76 | 4.5 | 30 | 28.1458 | 30 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 24.8982 | #10 | 10 | 65.736 | #6 | 10 | 66 | #6 | 0.435 | 1484.2818 | 40 | 55 | 20 | 61.248 | 0.61248 | 0.30624 | 800 | 34 | 48 | 28 | 47.9444 | 585.3234
18 | 2.45 | 44.1 | 75 | 120 | 26.4619 | 12 | 24.1398 | 41.8113 | 20 | 74.7 | 5.5 | 30 | 34.4005 | 40 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 30.4312 | #10 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 0.535 | 1825.496 | 40 | 55 | 20 | 75.328 | 0.75328 | 0.37664 | 800 | 34 | 48 | 28 | 47.9444 | 926.5376
18 | 2.45 | 44.1 | 100 | 120 | 34.8816 | 12 | 24.1398 | 41.8113 | 20 | 99.6 | 7.25 | 30 | 45.3461 | 50 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 40.1138 | #10 | 10 | 109.56 | #3 | 10 | 110 | #3 | 0.7075 | 2414.0905 | 40 | 55 | 20 | 99.616 | 0.99616 | 0.49808 | 800 | 34 | 48 | 28 | 47.9444 | 1515.1321
18 | 2.45 | 44.1 | 125 | 208 | 25.6754 | 12 | 24.1398 | 41.8113 | 20 | 124.5 | 9.25 | 30 | 33.3781 | 40 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 29.5267 | #10 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 0.8975 | 3062.3974 | 40 | 55 | 20 | 126.368 | 1.2637 | 0.63184 | 800 | 34 | 48 | 28 | 47.9444 | 2163.4391
18 | 2.45 | 44.1 | 150 | 208 | 30.5329 | 12 | 24.1398 | 41.8113 | 20 | 149.4 | 11 | 30 | 39.6928 | 40 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 35.1129 | #10 | 10 | 164.34 | #1 | 10 | 165 | #1 | 1.07 | 3650.9919 | 40 | 55 | 20 | 150.656 | 1.5066 | 0.75328 | 800 | 34 | 48 | 28 | 47.9444 | 2752.0336
18 | 2.45 | 44.1 | 175 | 208 | 36.0844 | 12 | 24.1398 | 41.8113 | 20 | 174.3 | 13 | 30 | 46.9097 | 50 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 41.4971 | #8 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 1.26 | 4299.2989 | 40 | 55 | 20 | 177.408 | 1.7741 | 0.88704 | 1200 | 38 | 70 | 28 | 71.5556 | 2957.6323
18 | 2.45 | 44.1 | 200 | 208 | 40.248 | 12 | 24.1398 | 41.8113 | 20 | 199.2 | 14.5 | 30 | 52.3224 | 60 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 46.2852 | #8 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 1.415 | 4828.1809 | 40 | 55 | 20 | 199.232 | 1.9923 | 0.99616 | 1200 | 38 | 70 | 28 | 71.5556 | 3486.5143
18 | 2.45 | 44.1 | 250 | 480 | 22.252 | 12 | 24.1398 | 41.8113 | 20 | 249 | 18.5 | 30 | 28.9277 | 30 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 25.5898 | #10 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 1.795 | 6124.7949 | 40 | 55 | 20 | 252.736 | 2.5274 | 1.2637 | 1200 | 38 | 70 | 28 | 71.5556 | 4783.1282
18 | 2.45 | 44.1 | 300 | 480 | 26.4619 | 12 | 24.1398 | 41.8113 | 20 | 298.8 | 22 | 30 | 34.4005 | 40 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 30.4312 | #10 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 2.14 | 7301.9839 | 40 | 55 | 20 | 301.312 | 3.0131 | 1.5066 | 1200 | 38 | 70 | 28 | 71.5556 | 5960.3172
18 | 2.45 | 44.1 | 350 | 480 | 31.2731 | 12 | 24.1398 | 41.8113 | 20 | 348.6 | 26 | 30 | 40.6551 | 50 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 35.9641 | #10 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 2.52 | 8598.5978 | 40 | 55 | 20 | 354.816 | 3.5482 | 1.7741 | 1200 | 38 | 70 | 28 | 71.5556 | 7256.9312
18 | 2.45 | 44.1 | 400 | 480 | 34.8816 | 12 | 24.1398 | 41.8113 | 20 | 398.4 | 29 | 30 | 45.3461 | 50 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 40.1138 | #10 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 2.83 | 9656.3619 | 40 | 55 | 20 | 398.464 | 3.9846 | 1.9923 | 1200 | 38 | 70 | 28 | 71.5556 | 8314.6952
18 | 2.45 | 44.1 | 450 | 480 | 39.6928 | 12 | 24.1398 | 41.8113 | 20 | 448.2 | 33 | 30 | 51.6007 | 60 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 45.6468 | #8 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 3.21 | 10952.9758 | 40 | 55 | 20 | 451.968 | 4.5197 | 2.2598 | 1200 | 38 | 70 | 28 | 71.5556 | 9611.3092
18 | 2.45 | 44.1 | 500 | 480 | 44.5041 | 12 | 24.1398 | 41.8113 | 20 | 498 | 37 | 30 | 57.8553 | 60 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 51.1797 | #8 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 3.59 | 12249.5898 | 40 | 55 | 20 | 505.472 | 5.0547 | 2.5274 | 1200 | 38 | 70 | 28 | 71.5556 | 10907.9231
18 | 2.45 | 44.1 | 600 | 480 | 52.9238 | 12 | 24.1398 | 41.8113 | 20 | 597.6 | 44 | 30 | 68.8009 | 70 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 60.8623 | #6 | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 4.28 | 14603.9678 | 40 | 55 | 20 | 602.624 | 6.0262 | 3.0131 | 1200 | 38 | 70 | 28 | 71.5556 | 13262.3011
18 | 2.45 | 44.1 | 700 | 480 | 61.3435 | 12 | 24.1398 | 41.8113 | 20 | 697.2 | 51 | 30 | 79.7465 | 80 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 70.545 | #6 | 10 | 766.92 | Buss | 10 | 770 | Buss | 4.97 | 16958.3457 | 40 | 55 | 20 | 699.776 | 6.9978 | 3.4989 | 1200 | 38 | 70 | 28 | 71.5556 | 15616.6791
18 | 2.45 | 44.1 | 800 | 480 | 69.7632 | 12 | 24.1398 | 41.8113 | 20 | 796.8 | 58 | 30 | 90.6921 | 100 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 80.2276 | #6 | 10 | 876.48 | Buss | 10 | 880 | Buss | 5.66 | 19312.7237 | 40 | 55 | 20 | 796.928 | 7.9693 | 3.9846 | 1200 | 38 | 70 | 28 | 71.5556 | 17971.0571
18 | 2.45 | 44.1 | 900 | 480 | 78.1828 | 12 | 24.1398 | 41.8113 | 20 | 896.4 | 65 | 30 | 101.6377 | 110 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 89.9103 | #4 | 10 | 986.04 | Buss | 10 | 990 | Buss | 6.35 | 21667.1017 | 40 | 55 | 20 | 894.08 | 8.9408 | 4.4704 | 1200 | 38 | 70 | 28 | 71.5556 | 20325.435
18 | 2.45 | 44.1 | 1000 | 480 | 87.8054 | 12 | 24.1398 | 41.8113 | 20 | 996 | 73 | 30 | 114.147 | 125 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 100.9762 | #4 | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 7.11 | 24260.3296 | 40 | 55 | 20 | 1001.088 | 10.0109 | 5.0054 | 1200 | 38 | 70 | 28 | 71.5556 | 22918.663
18 | 2.45 | 44.1 | 1100 | 480 | 96.225 | 12 | 24.1398 | 41.8113 | 20 | 1095.6 | 80 | 30 | 125.0926 | 125 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 110.6588 | #3 | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 7.8 | 26614.7076 | 40 | 55 | 20 | 1098.24 | 10.9824 | 5.4912 | 1200 | 38 | 70 | 28 | 71.5556 | 25273.0409
18 | 2.45 | 44.1 | 1200 | 480 | 104.6447 | 12 | 24.1398 | 41.8113 | 20 | 1195.2 | 87 | 30 | 136.0382 | 150 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 120.3414 | #3 | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 8.49 | 28969.0856 | 40 | 55 | 20 | 1195.392 | 11.9539 | 5.977 | 1200 | 38 | 70 | 28 | 71.5556 | 27627.4189
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
48 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
24 | 2.45 | 58.8 | 5 | 120 | 2.4056 | 12 | 31.1864 | 54.0164 | 20 | 4.98 | 0.5 | 30 | 3.1273 | 5 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 2.7665 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.045 | 153.5464 | 40 | 55 | 20 | 6.336 | 0.06336 | 0.03168 | 450 | 24 | 30 | 16 | 19.3333 | -208.9536
24 | 2.45 | 58.8 | 10 | 120 | 4.8113 | 12 | 31.1864 | 54.0164 | 20 | 9.96 | 1 | 30 | 6.2546 | 10 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 5.5329 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.09 | 307.0928 | 40 | 55 | 20 | 12.672 | 0.12672 | 0.06336 | 450 | 24 | 30 | 16 | 19.3333 | -55.4072
24 | 2.45 | 58.8 | 15 | 120 | 7.2169 | 12 | 31.1864 | 54.0164 | 20 | 14.94 | 1.5 | 30 | 9.3819 | 10 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 8.2994 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.135 | 460.6392 | 40 | 55 | 20 | 19.008 | 0.19008 | 0.09504 | 600 | 24 | 48 | 16 | 29.3333 | -89.3608
24 | 2.45 | 58.8 | 20 | 120 | 9.6225 | 12 | 31.1864 | 54.0164 | 20 | 19.92 | 2 | 30 | 12.5093 | 15 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 11.0659 | #10 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.18 | 614.1856 | 40 | 55 | 20 | 25.344 | 0.25344 | 0.12672 | 600 | 24 | 48 | 16 | 29.3333 | 64.1856
24 | 2.45 | 58.8 | 25 | 120 | 12.0281 | 12 | 31.1864 | 54.0164 | 20 | 24.9 | 2.5 | 30 | 15.6366 | 20 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 13.8324 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.225 | 767.732 | 40 | 55 | 20 | 31.68 | 0.3168 | 0.1584 | 600 | 24 | 48 | 16 | 29.3333 | 217.732
24 | 2.45 | 58.8 | 30 | 120 | 14.4338 | 12 | 31.1864 | 54.0164 | 20 | 29.88 | 3 | 30 | 18.7639 | 20 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 16.5988 | #10 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.27 | 921.2783 | 40 | 55 | 20 | 38.016 | 0.38016 | 0.19008 | 600 | 24 | 48 | 16 | 29.3333 | 371.2783
24 | 2.45 | 58.8 | 35 | 120 | 16.8394 | 12 | 31.1864 | 54.0164 | 20 | 34.86 | 3.5 | 30 | 21.8912 | 25 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 19.3653 | #10 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 0.315 | 1074.8247 | 40 | 55 | 20 | 44.352 | 0.44352 | 0.22176 | 600 | 24 | 48 | 16 | 29.3333 | 524.8247
24 | 2.45 | 58.8 | 40 | 120 | 18.0422 | 12 | 31.1864 | 54.0164 | 20 | 39.84 | 3.75 | 30 | 23.4549 | 25 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 20.7485 | #10 | 10 | 43.824 | #8 | 10 | 44 | #8 | 0.3425 | 1168.6586 | 40 | 55 | 20 | 48.224 | 0.48224 | 0.24112 | 600 | 24 | 48 | 16 | 29.3333 | 618.6586
24 | 2.45 | 58.8 | 50 | 120 | 22.8534 | 12 | 31.1864 | 54.0164 | 20 | 49.8 | 4.75 | 30 | 29.7095 | 30 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 26.2815 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 0.4325 | 1475.7514 | 40 | 55 | 20 | 60.896 | 0.60896 | 0.30448 | 800 | 34 | 48 | 28 | 47.9444 | 576.7931
24 | 2.45 | 58.8 | 60 | 120 | 27.6647 | 12 | 31.1864 | 54.0164 | 20 | 59.76 | 5.75 | 30 | 35.9641 | 40 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 31.8144 | #10 | 10 | 65.736 | #6 | 10 | 66 | #6 | 0.5225 | 1782.8442 | 40 | 55 | 20 | 73.568 | 0.73568 | 0.36784 | 800 | 34 | 48 | 28 | 47.9444 | 883.8859
24 | 2.45 | 58.8 | 75 | 120 | 33.6788 | 12 | 31.1864 | 54.0164 | 20 | 74.7 | 7 | 30 | 43.7824 | 50 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 38.7306 | #10 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 0.64 | 2183.7709 | 40 | 55 | 20 | 90.112 | 0.90112 | 0.45056 | 800 | 34 | 48 | 28 | 47.9444 | 1284.8125
24 | 2.45 | 58.8 | 100 | 208 | 26.3694 | 12 | 31.1864 | 54.0164 | 20 | 99.6 | 9.5 | 30 | 34.2802 | 40 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 30.3248 | #10 | 10 | 109.56 | #3 | 10 | 110 | #3 | 0.865 | 2951.5028 | 40 | 55 | 20 | 121.792 | 1.2179 | 0.60896 | 800 | 34 | 48 | 28 | 47.9444 | 2052.5445
24 | 2.45 | 58.8 | 125 | 208 | 33.3087 | 12 | 31.1864 | 54.0164 | 20 | 124.5 | 12 | 30 | 43.3013 | 50 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 38.305 | #10 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 1.09 | 3719.2348 | 40 | 55 | 20 | 153.472 | 1.5347 | 0.76736 | 800 | 34 | 48 | 28 | 47.9444 | 2820.2764
24 | 2.45 | 58.8 | 150 | 208 | 38.8601 | 12 | 31.1864 | 54.0164 | 20 | 149.4 | 14 | 30 | 50.5181 | 60 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 44.6891 | #8 | 10 | 164.34 | #1 | 10 | 165 | #1 | 1.28 | 4367.5418 | 40 | 55 | 20 | 180.224 | 1.8022 | 0.90112 | 800 | 34 | 48 | 28 | 47.9444 | 3468.5834
24 | 2.45 | 58.8 | 175 | 240 | 39.6928 | 12 | 31.1864 | 54.0164 | 20 | 174.3 | 16.5 | 30 | 51.6007 | 60 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 45.6468 | #8 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 1.505 | 5135.2737 | 40 | 55 | 20 | 211.904 | 2.119 | 1.0595 | 1200 | 38 | 70 | 28 | 71.5556 | 3793.607
24 | 2.45 | 58.8 | 200 | 480 | 22.8534 | 12 | 31.1864 | 54.0164 | 20 | 199.2 | 19 | 30 | 29.7095 | 30 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 26.2815 | #10 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 1.73 | 5903.0057 | 40 | 55 | 20 | 243.584 | 2.4358 | 1.2179 | 1200 | 38 | 70 | 28 | 71.5556 | 4561.339
24 | 2.45 | 58.8 | 250 | 480 | 28.8675 | 12 | 31.1864 | 54.0164 | 20 | 249 | 24 | 30 | 37.5278 | 40 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 33.1976 | #10 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 2.18 | 7438.4696 | 40 | 55 | 20 | 306.944 | 3.0694 | 1.5347 | 1200 | 38 | 70 | 28 | 71.5556 | 6096.8029
24 | 2.45 | 58.8 | 300 | 480 | 33.6788 | 12 | 31.1864 | 54.0164 | 20 | 298.8 | 28 | 30 | 43.7824 | 50 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 38.7306 | #10 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 2.56 | 8735.0835 | 40 | 55 | 20 | 360.448 | 3.6045 | 1.8022 | 1200 | 38 | 70 | 28 | 71.5556 | 7393.4169
24 | 2.45 | 58.8 | 350 | 480 | 39.6928 | 12 | 31.1864 | 54.0164 | 20 | 348.6 | 33 | 30 | 51.6007 | 60 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 45.6468 | #8 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 3.01 | 10270.5474 | 40 | 55 | 20 | 423.808 | 4.2381 | 2.119 | 1200 | 38 | 70 | 28 | 71.5556 | 8928.8808
24 | 2.45 | 58.8 | 400 | 480 | 45.7069 | 12 | 31.1864 | 54.0164 | 20 | 398.4 | 38 | 30 | 59.419 | 60 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 52.5629 | #8 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 3.46 | 11806.0113 | 40 | 55 | 20 | 487.168 | 4.8717 | 2.4358 | 1200 | 38 | 70 | 28 | 71.5556 | 10464.3447
24 | 2.45 | 58.8 | 450 | 480 | 50.5181 | 12 | 31.1864 | 54.0164 | 20 | 448.2 | 42 | 30 | 65.6736 | 70 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 58.0959 | #8 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 3.84 | 13102.6253 | 40 | 55 | 20 | 540.672 | 5.4067 | 2.7034 | 1200 | 38 | 70 | 28 | 71.5556 | 11760.9586
24 | 2.45 | 58.8 | 500 | 480 | 56.5322 | 12 | 31.1864 | 54.0164 | 20 | 498 | 47 | 30 | 73.4919 | 80 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 65.012 | #6 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 4.29 | 14638.0892 | 40 | 55 | 20 | 604.032 | 6.0403 | 3.0202 | 1200 | 38 | 70 | 28 | 71.5556 | 13296.4225
24 | 2.45 | 58.8 | 600 | 480 | 67.3575 | 12 | 31.1864 | 54.0164 | 20 | 597.6 | 56 | 30 | 87.5648 | 90 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 77.4612 | #6 | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 5.12 | 17470.167 | 40 | 55 | 20 | 720.896 | 7.209 | 3.6045 | 1200 | 38 | 70 | 28 | 71.5556 | 16128.5004
24 | 2.45 | 58.8 | 700 | 480 | 79.3857 | 12 | 31.1864 | 54.0164 | 20 | 697.2 | 66 | 30 | 103.2014 | 110 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 91.2935 | #4 | 10 | 766.92 | Buss | 10 | 770 | Buss | 6.02 | 20541.0948 | 40 | 55 | 20 | 847.616 | 8.4762 | 4.2381 | 1200 | 38 | 70 | 28 | 71.5556 | 19199.4282
24 | 2.45 | 58.8 | 800 | 480 | 90.211 | 12 | 31.1864 | 54.0164 | 20 | 796.8 | 75 | 30 | 117.2743 | 125 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 103.7426 | #4 | 10 | 876.48 | Buss | 10 | 880 | Buss | 6.85 | 23373.1727 | 40 | 55 | 20 | 964.48 | 9.6448 | 4.8224 | 1200 | 38 | 70 | 28 | 71.5556 | 22031.506
24 | 2.45 | 58.8 | 900 | 480 | 101.0363 | 12 | 31.1864 | 54.0164 | 20 | 896.4 | 84 | 30 | 131.3472 | 150 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 116.1917 | #3 | 10 | 986.04 | Buss | 10 | 990 | Buss | 7.68 | 26205.2506 | 40 | 55 | 20 | 1081.344 | 10.8134 | 5.4067 | 1200 | 38 | 70 | 28 | 71.5556 | 24863.5839
24 | 2.45 | 58.8 | 1000 | 480 | 113.0644 | 12 | 31.1864 | 54.0164 | 20 | 996 | 94 | 30 | 146.9838 | 150 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 130.0241 | #2 | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 8.58 | 29276.1784 | 40 | 55 | 20 | 1208.064 | 12.0806 | 6.0403 | 1200 | 38 | 70 | 28 | 71.5556 | 27934.5117
24 | 2.45 | 58.8 | 1100 | 480 | 123.8897 | 12 | 31.1864 | 54.0164 | 20 | 1095.6 | 103 | 30 | 161.0567 | 175 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 142.4732 | #1 | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 9.41 | 32108.2562 | 40 | 55 | 20 | 1324.928 | 13.2493 | 6.6246 | 1200 | 38 | 70 | 28 | 71.5556 | 30766.5896
24 | 2.45 | 58.8 | 1200 | 480 | 134.7151 | 12 | 31.1864 | 54.0164 | 20 | 1195.2 | 112 | 30 | 175.1296 | 175 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 154.9223 | #1 | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 10.24 | 34940.3341 | 40 | 55 | 20 | 1441.792 | 14.4179 | 7.209 | 1200 | 38 | 70 | 28 | 71.5556 | 33598.6674
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
72 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
36 | 2.45 | 88.2 | 5 | 120 | 3.6084 | 12 | 45.2796 | 78.4265 | 20 | 4.98 | 0.75 | 30 | 4.691 | 5 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 4.1497 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.0625 | 213.2589 | 40 | 55 | 20 | 8.8 | 0.088 | 0.044 | 450 | 24 | 30 | 16 | 19.3333 | -149.2411
36 | 2.45 | 88.2 | 10 | 120 | 7.2169 | 12 | 45.2796 | 78.4265 | 20 | 9.96 | 1.5 | 30 | 9.3819 | 10 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 8.2994 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.125 | 426.5178 | 40 | 55 | 20 | 17.6 | 0.176 | 0.088 | 450 | 24 | 30 | 16 | 19.3333 | 64.0178
36 | 2.45 | 88.2 | 15 | 120 | 10.8253 | 12 | 45.2796 | 78.4265 | 20 | 14.94 | 2.25 | 30 | 14.0729 | 15 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 12.4491 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.1875 | 639.7766 | 40 | 55 | 20 | 26.4 | 0.264 | 0.132 | 600 | 24 | 48 | 16 | 29.3333 | 89.7766
36 | 2.45 | 88.2 | 20 | 120 | 13.2309 | 12 | 45.2796 | 78.4265 | 20 | 19.92 | 2.75 | 30 | 17.2002 | 20 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 15.2156 | #10 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.2325 | 793.323 | 40 | 55 | 20 | 32.736 | 0.32736 | 0.16368 | 600 | 24 | 48 | 16 | 29.3333 | 243.323
36 | 2.45 | 88.2 | 25 | 120 | 16.8394 | 12 | 45.2796 | 78.4265 | 20 | 24.9 | 3.5 | 30 | 21.8912 | 25 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 19.3653 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.295 | 1006.5819 | 40 | 55 | 20 | 41.536 | 0.41536 | 0.20768 | 600 | 24 | 48 | 16 | 29.3333 | 456.5819
36 | 2.45 | 88.2 | 30 | 120 | 20.4478 | 12 | 45.2796 | 78.4265 | 20 | 29.88 | 4.25 | 30 | 26.5822 | 30 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 23.515 | #10 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.3575 | 1219.8408 | 40 | 55 | 20 | 50.336 | 0.50336 | 0.25168 | 600 | 24 | 48 | 16 | 29.3333 | 669.8408
36 | 2.45 | 88.2 | 35 | 120 | 22.8534 | 12 | 45.2796 | 78.4265 | 20 | 34.86 | 4.75 | 30 | 29.7095 | 30 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 26.2815 | #10 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 0.4025 | 1373.3872 | 40 | 55 | 20 | 56.672 | 0.56672 | 0.28336 | 600 | 24 | 48 | 16 | 29.3333 | 823.3872
36 | 2.45 | 88.2 | 40 | 120 | 26.4619 | 12 | 45.2796 | 78.4265 | 20 | 39.84 | 5.5 | 30 | 34.4005 | 40 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 30.4312 | #10 | 10 | 43.824 | #8 | 10 | 44 | #8 | 0.465 | 1586.646 | 40 | 55 | 20 | 65.472 | 0.65472 | 0.32736 | 600 | 24 | 48 | 16 | 29.3333 | 1036.646
36 | 2.45 | 88.2 | 50 | 120 | 33.6788 | 12 | 45.2796 | 78.4265 | 20 | 49.8 | 7 | 30 | 43.7824 | 50 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 38.7306 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 0.59 | 2013.1638 | 40 | 55 | 20 | 83.072 | 0.83072 | 0.41536 | 800 | 34 | 48 | 28 | 47.9444 | 1114.2054
36 | 2.45 | 88.2 | 60 | 120 | 39.6928 | 12 | 45.2796 | 78.4265 | 20 | 59.76 | 8.25 | 30 | 51.6007 | 60 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 45.6468 | #8 | 10 | 65.736 | #6 | 10 | 66 | #6 | 0.6975 | 2379.969 | 40 | 55 | 20 | 98.208 | 0.98208 | 0.49104 | 800 | 34 | 48 | 28 | 47.9444 | 1481.0107
36 | 2.45 | 88.2 | 75 | 208 | 29.1451 | 12 | 45.2796 | 78.4265 | 20 | 74.7 | 10.5 | 30 | 37.8886 | 40 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 33.5168 | #10 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 0.885 | 3019.7457 | 40 | 55 | 20 | 124.608 | 1.2461 | 0.62304 | 800 | 34 | 48 | 28 | 47.9444 | 2120.7873
36 | 2.45 | 88.2 | 100 | 208 | 38.8601 | 12 | 45.2796 | 78.4265 | 20 | 99.6 | 14 | 30 | 50.5181 | 60 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 44.6891 | #8 | 10 | 109.56 | #3 | 10 | 110 | #3 | 1.18 | 4026.3276 | 40 | 55 | 20 | 166.144 | 1.6614 | 0.83072 | 800 | 34 | 48 | 28 | 47.9444 | 3127.3692
36 | 2.45 | 88.2 | 125 | 240 | 40.8956 | 12 | 45.2796 | 78.4265 | 20 | 124.5 | 17 | 30 | 53.1643 | 60 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 47.03 | #8 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 1.44 | 4913.4845 | 40 | 55 | 20 | 202.752 | 2.0275 | 1.0138 | 800 | 34 | 48 | 28 | 47.9444 | 4014.5261
36 | 2.45 | 88.2 | 150 | 480 | 25.2591 | 12 | 45.2796 | 78.4265 | 20 | 149.4 | 21 | 30 | 32.8368 | 40 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 29.0479 | #10 | 10 | 164.34 | #1 | 10 | 165 | #1 | 1.77 | 6039.4913 | 40 | 55 | 20 | 249.216 | 2.4922 | 1.2461 | 800 | 34 | 48 | 28 | 47.9444 | 5140.533
36 | 2.45 | 88.2 | 175 | 480 | 28.8675 | 12 | 45.2796 | 78.4265 | 20 | 174.3 | 24 | 30 | 37.5278 | 40 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 33.1976 | #10 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 2.03 | 6926.6483 | 40 | 55 | 20 | 285.824 | 2.8582 | 1.4291 | 1200 | 38 | 70 | 28 | 71.5556 | 5584.9816
36 | 2.45 | 88.2 | 200 | 480 | 33.6788 | 12 | 45.2796 | 78.4265 | 20 | 199.2 | 28 | 30 | 43.7824 | 50 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 38.7306 | #10 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 2.36 | 8052.6551 | 40 | 55 | 20 | 332.288 | 3.3229 | 1.6614 | 1200 | 38 | 70 | 28 | 71.5556 | 6710.9885
36 | 2.45 | 88.2 | 250 | 480 | 40.8956 | 12 | 45.2796 | 78.4265 | 20 | 249 | 34 | 30 | 53.1643 | 60 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 47.03 | #8 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 2.88 | 9826.969 | 40 | 55 | 20 | 405.504 | 4.055 | 2.0275 | 1200 | 38 | 70 | 28 | 71.5556 | 8485.3023
36 | 2.45 | 88.2 | 300 | 480 | 49.3153 | 12 | 45.2796 | 78.4265 | 20 | 298.8 | 41 | 30 | 64.1099 | 70 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 56.7126 | #8 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 3.47 | 11840.1327 | 40 | 55 | 20 | 488.576 | 4.8858 | 2.4429 | 1200 | 38 | 70 | 28 | 71.5556 | 10498.4661
36 | 2.45 | 88.2 | 350 | 480 | 57.735 | 12 | 45.2796 | 78.4265 | 20 | 348.6 | 48 | 30 | 75.0555 | 80 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 66.3953 | #6 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 4.06 | 13853.2965 | 40 | 55 | 20 | 571.648 | 5.7165 | 2.8582 | 1200 | 38 | 70 | 28 | 71.5556 | 12511.6299
36 | 2.45 | 88.2 | 400 | 480 | 66.1547 | 12 | 45.2796 | 78.4265 | 20 | 398.4 | 55 | 30 | 86.0011 | 90 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 76.0779 | #6 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 4.65 | 15866.4603 | 40 | 55 | 20 | 654.72 | 6.5472 | 3.2736 | 1200 | 38 | 70 | 28 | 71.5556 | 14524.7936
36 | 2.45 | 88.2 | 450 | 480 | 73.3716 | 12 | 45.2796 | 78.4265 | 20 | 448.2 | 61 | 30 | 95.3831 | 100 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 84.3773 | #4 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 5.17 | 17640.7741 | 40 | 55 | 20 | 727.936 | 7.2794 | 3.6397 | 1200 | 38 | 70 | 28 | 71.5556 | 16299.1075
36 | 2.45 | 88.2 | 500 | 480 | 81.7913 | 12 | 45.2796 | 78.4265 | 20 | 498 | 68 | 30 | 106.3287 | 110 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 94.06 | #4 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 5.76 | 19653.9379 | 40 | 55 | 20 | 811.008 | 8.1101 | 4.055 | 1200 | 38 | 70 | 28 | 71.5556 | 18312.2713
36 | 2.45 | 88.2 | 600 | 480 | 98.6307 | 12 | 45.2796 | 78.4265 | 20 | 597.6 | 82 | 30 | 128.2199 | 150 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 113.4253 | #3 | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 6.94 | 23680.2655 | 40 | 55 | 20 | 977.152 | 9.7715 | 4.8858 | 1200 | 38 | 70 | 28 | 71.5556 | 22338.5988
36 | 2.45 | 88.2 | 700 | 480 | 114.2672 | 12 | 45.2796 | 78.4265 | 20 | 697.2 | 95 | 30 | 148.5474 | 150 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 131.4073 | #2 | 10 | 766.92 | Buss | 10 | 770 | Buss | 8.05 | 27467.7431 | 40 | 55 | 20 | 1133.44 | 11.3344 | 5.6672 | 1200 | 38 | 70 | 28 | 71.5556 | 26126.0764
36 | 2.45 | 88.2 | 800 | 480 | 131.1066 | 12 | 45.2796 | 78.4265 | 20 | 796.8 | 109 | 30 | 170.4386 | 175 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 150.7726 | #1 | 10 | 876.48 | Buss | 10 | 880 | Buss | 9.23 | 31494.0707 | 40 | 55 | 20 | 1299.584 | 12.9958 | 6.4979 | 1200 | 38 | 70 | 28 | 71.5556 | 30152.404
36 | 2.45 | 88.2 | 900 | 480 | 146.7432 | 12 | 45.2796 | 78.4265 | 20 | 896.4 | 122 | 30 | 190.7662 | 200 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 168.7547 | #1/0 | 10 | 986.04 | Buss | 10 | 990 | Buss | 10.34 | 35281.5483 | 40 | 55 | 20 | 1455.872 | 14.5587 | 7.2794 | 1200 | 38 | 70 | 28 | 71.5556 | 33939.8816
36 | 2.45 | 88.2 | 1000 | 480 | 163.5826 | 12 | 45.2796 | 78.4265 | 20 | 996 | 136 | 30 | 212.6573 | 225 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 188.12 | #1/0 | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 11.52 | 39307.8758 | 40 | 55 | 20 | 1622.016 | 16.2202 | 8.1101 | 1200 | 38 | 70 | 28 | 71.5556 | 37966.2092
36 | 2.45 | 88.2 | 1100 | 480 | 179.2191 | 12 | 45.2796 | 78.4265 | 20 | 1095.6 | 149 | 30 | 232.9849 | 250 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 206.102 | #2/0 | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 12.63 | 43095.3535 | 40 | 55 | 20 | 1778.304 | 17.783 | 8.8915 | 1200 | 38 | 70 | 28 | 71.5556 | 41753.6868
36 | 2.45 | 88.2 | 1200 | 480 | 196.0585 | 12 | 45.2796 | 78.4265 | 20 | 1195.2 | 163 | 30 | 254.8761 | 300 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 225.4673 | #2/0 | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 13.81 | 47121.681 | 40 | 55 | 20 | 1944.448 | 19.4445 | 9.7222 | 1200 | 38 | 70 | 28 | 71.5556 | 45780.0144
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
120 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
60 | 2.45 | 147 | 5 | 120 | 6.0141 | 12 | 73.4659 | 127.2467 | 20 | 4.98 | 1.25 | 30 | 7.8183 | 10 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 6.9162 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.0975 | 332.6838 | 40 | 55 | 20 | 13.728 | 0.13728 | 0.06864 | 450 | 24 | 30 | 16 | 19.3333 | -29.8162
60 | 2.45 | 147 | 10 | 120 | 10.8253 | 12 | 73.4659 | 127.2467 | 20 | 9.96 | 2.25 | 30 | 14.0729 | 15 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 12.4491 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.1775 | 605.6552 | 40 | 55 | 20 | 24.992 | 0.24992 | 0.12496 | 450 | 24 | 30 | 16 | 19.3333 | 243.1552
60 | 2.45 | 147 | 15 | 120 | 16.8394 | 12 | 73.4659 | 127.2467 | 20 | 14.94 | 3.5 | 30 | 21.8912 | 25 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 19.3653 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.275 | 938.3391 | 40 | 55 | 20 | 38.72 | 0.3872 | 0.1936 | 600 | 24 | 48 | 16 | 29.3333 | 388.3391
60 | 2.45 | 147 | 20 | 120 | 21.6506 | 12 | 73.4659 | 127.2467 | 20 | 19.92 | 4.5 | 30 | 28.1458 | 30 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 24.8982 | #10 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.355 | 1211.3104 | 40 | 55 | 20 | 49.984 | 0.49984 | 0.24992 | 600 | 24 | 48 | 16 | 29.3333 | 661.3104
60 | 2.45 | 147 | 25 | 120 | 26.4619 | 12 | 73.4659 | 127.2467 | 20 | 24.9 | 5.5 | 30 | 34.4005 | 40 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 30.4312 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.435 | 1484.2818 | 40 | 55 | 20 | 61.248 | 0.61248 | 0.30624 | 600 | 24 | 48 | 16 | 29.3333 | 934.2818
60 | 2.45 | 176 | 30 | 120 | 37.2872 | 12 | 84.3674 | 146.1286 | 20 | 29.88 | 7.75 | 30 | 48.4734 | 50 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 42.8803 | #8 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.6025 | 2055.8156 | 40 | 55 | 20 | 84.832 | 0.84832 | 0.42416 | 600 | 24 | 48 | 16 | 29.3333 | 1505.8156
60 | 2.45 | 166 | 35 | 120 | 40.8956 | 12 | 79.5738 | 137.8258 | 20 | 34.86 | 8.5 | 30 | 53.1643 | 60 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 47.03 | #8 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 0.665 | 2269.0744 | 40 | 55 | 20 | 93.632 | 0.93632 | 0.46816 | 600 | 24 | 48 | 16 | 29.3333 | 1719.0744
60 | 2.45 | 147 | 40 | 120 | 43.3013 | 12 | 73.4659 | 127.2467 | 20 | 39.84 | 9 | 30 | 56.2917 | 60 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 49.7965 | #8 | 10 | 43.824 | #8 | 10 | 44 | #8 | 0.71 | 2422.6208 | 40 | 55 | 20 | 99.968 | 0.99968 | 0.49984 | 600 | 24 | 48 | 16 | 29.3333 | 1872.6208
60 | 2.45 | 147 | 50 | 208 | 30.5329 | 12 | 73.4659 | 127.2467 | 20 | 49.8 | 11 | 30 | 39.6928 | 40 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 35.1129 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 0.87 | 2968.5635 | 40 | 55 | 20 | 122.496 | 1.225 | 0.61248 | 800 | 34 | 48 | 28 | 47.9444 | 2069.6052
60 | 2.45 | 147 | 60 | 208 | 37.4723 | 12 | 73.4659 | 127.2467 | 20 | 59.76 | 13.5 | 30 | 48.7139 | 50 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 43.0931 | #8 | 10 | 65.736 | #6 | 10 | 66 | #6 | 1.065 | 3633.9312 | 40 | 55 | 20 | 149.952 | 1.4995 | 0.74976 | 800 | 34 | 48 | 28 | 47.9444 | 2734.9729
60 | 2.45 | 147 | 75 | 240 | 39.6928 | 12 | 73.4659 | 127.2467 | 20 | 74.7 | 16.5 | 30 | 51.6007 | 60 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 45.6468 | #8 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 1.305 | 4452.8453 | 40 | 55 | 20 | 183.744 | 1.8374 | 0.91872 | 800 | 34 | 48 | 28 | 47.9444 | 3553.887
60 | 2.45 | 147 | 100 | 480 | 26.4619 | 12 | 73.4659 | 127.2467 | 20 | 99.6 | 22 | 30 | 34.4005 | 40 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 30.4312 | #10 | 10 | 109.56 | #3 | 10 | 110 | #3 | 1.74 | 5937.1271 | 40 | 55 | 20 | 244.992 | 2.4499 | 1.225 | 800 | 34 | 48 | 28 | 47.9444 | 5038.1687
60 | 2.45 | 147 | 125 | 480 | 33.6788 | 12 | 73.4659 | 127.2467 | 20 | 124.5 | 28 | 30 | 43.7824 | 50 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 38.7306 | #10 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 2.21 | 7540.8338 | 40 | 55 | 20 | 311.168 | 3.1117 | 1.5558 | 800 | 34 | 48 | 28 | 47.9444 | 6641.8755
60 | 2.45 | 147 | 150 | 480 | 39.6928 | 12 | 73.4659 | 127.2467 | 20 | 149.4 | 33 | 30 | 51.6007 | 60 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 45.6468 | #8 | 10 | 164.34 | #1 | 10 | 165 | #1 | 2.61 | 8905.6906 | 40 | 55 | 20 | 367.488 | 3.6749 | 1.8374 | 800 | 34 | 48 | 28 | 47.9444 | 8006.7323
60 | 2.45 | 147 | 175 | 480 | 46.9097 | 12 | 73.4659 | 127.2467 | 20 | 174.3 | 39 | 30 | 60.9826 | 60 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 53.9462 | #8 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 3.08 | 10509.3974 | 40 | 55 | 20 | 433.664 | 4.3366 | 2.1683 | 1200 | 38 | 70 | 28 | 71.5556 | 9167.7307
60 | 2.45 | 147 | 200 | 480 | 52.9238 | 12 | 73.4659 | 127.2467 | 20 | 199.2 | 44 | 30 | 68.8009 | 70 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 60.8623 | #6 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 3.48 | 11874.2542 | 40 | 55 | 20 | 489.984 | 4.8998 | 2.4499 | 1200 | 38 | 70 | 28 | 71.5556 | 10532.5875
60 | 2.45 | 147 | 250 | 480 | 66.1547 | 12 | 73.4659 | 127.2467 | 20 | 249 | 55 | 30 | 86.0011 | 90 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 76.0779 | #6 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 4.35 | 14842.8177 | 40 | 55 | 20 | 612.48 | 6.1248 | 3.0624 | 1200 | 38 | 70 | 28 | 71.5556 | 13501.151
60 | 2.45 | 147 | 300 | 480 | 79.3857 | 12 | 73.4659 | 127.2467 | 20 | 298.8 | 66 | 30 | 103.2014 | 110 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 91.2935 | #4 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 5.22 | 17811.3812 | 40 | 55 | 20 | 734.976 | 7.3498 | 3.6749 | 1200 | 38 | 70 | 28 | 71.5556 | 16469.7146
60 | 2.45 | 147 | 350 | 480 | 92.6166 | 12 | 73.4659 | 127.2467 | 20 | 348.6 | 77 | 30 | 120.4016 | 125 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 106.5091 | #3 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 6.09 | 20779.9448 | 40 | 55 | 20 | 857.472 | 8.5747 | 4.2874 | 1200 | 38 | 70 | 28 | 71.5556 | 19438.2781
60 | 2.45 | 147 | 400 | 480 | 105.8475 | 12 | 73.4659 | 127.2467 | 20 | 398.4 | 88 | 30 | 137.6018 | 150 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 121.7247 | #2 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 6.96 | 23748.5083 | 40 | 55 | 20 | 979.968 | 9.7997 | 4.8998 | 1200 | 38 | 70 | 28 | 71.5556 | 22406.8417
60 | 2.45 | 147 | 450 | 480 | 119.0785 | 12 | 73.4659 | 127.2467 | 20 | 448.2 | 99 | 30 | 154.802 | 175 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 136.9403 | #2 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 7.83 | 26717.0719 | 40 | 55 | 20 | 1102.464 | 11.0246 | 5.5123 | 1200 | 38 | 70 | 28 | 71.5556 | 25375.4052
60 | 2.45 | 147 | 500 | 480 | 132.3094 | 12 | 73.4659 | 127.2467 | 20 | 498 | 110 | 30 | 172.0023 | 175 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 152.1559 | #1 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 8.7 | 29685.6354 | 40 | 55 | 20 | 1224.96 | 12.2496 | 6.1248 | 1200 | 38 | 70 | 28 | 71.5556 | 28343.9687
60 | 2.45 | 147 | 600 | 480 | 158.7713 | 12 | 73.4659 | 127.2467 | 20 | 597.6 | 132 | 30 | 206.4027 | 225 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 182.587 | #1/0 | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 10.44 | 35622.7625 | 40 | 55 | 20 | 1469.952 | 14.6995 | 7.3498 | 1200 | 38 | 70 | 28 | 71.5556 | 34281.0958
60 | 2.45 | 147 | 700 | 480 | 185.2332 | 12 | 73.4659 | 127.2467 | 20 | 697.2 | 154 | 30 | 240.8032 | 250 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 213.0182 | #2/0 | 10 | 766.92 | Buss | 10 | 770 | Buss | 12.18 | 41559.8896 | 40 | 55 | 20 | 1714.944 | 17.1494 | 8.5747 | 1200 | 38 | 70 | 28 | 71.5556 | 40218.2229
60 | 2.45 | 147 | 800 | 480 | 211.6951 | 12 | 73.4659 | 127.2467 | 20 | 796.8 | 176 | 30 | 275.2036 | 300 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 243.4494 | #3/0 | 10 | 876.48 | Buss | 10 | 880 | Buss | 13.92 | 47497.0166 | 40 | 55 | 20 | 1959.936 | 19.5994 | 9.7997 | 1200 | 38 | 70 | 28 | 71.5556 | 46155.35
60 | 2.45 | 147 | 900 | 480 | 238.157 | 12 | 73.4659 | 127.2467 | 20 | 896.4 | 198 | 30 | 309.6041 | 350 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 273.8805 | #4/0 | 10 | 986.04 | Buss | 10 | 990 | Buss | 15.66 | 53434.1437 | 40 | 55 | 20 | 2204.928 | 22.0493 | 11.0246 | 1200 | 38 | 70 | 28 | 71.5556 | 52092.4771
60 | 2.45 | 147 | 1000 | 480 | 264.6189 | 12 | 73.4659 | 127.2467 | 20 | 996 | 220 | 30 | 344.0045 | 350 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 304.3117 | 250MCM | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 17.4 | 59371.2708 | 40 | 55 | 20 | 2449.92 | 24.4992 | 12.2496 | 1200 | 38 | 70 | 28 | 71.5556 | 58029.6041
60 | 2.45 | 147 | 1100 | 480 | 291.0808 | 12 | 73.4659 | 127.2467 | 20 | 1095.6 | 242 | 30 | 378.405 | 400 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 334.7429 | 250MCM | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 19.14 | 65308.3979 | 40 | 55 | 20 | 2694.912 | 26.9491 | 13.4746 | 1200 | 38 | 70 | 28 | 71.5556 | 63966.7312
60 | 2.45 | 147 | 1200 | 480 | 317.5426 | 12 | 73.4659 | 127.2467 | 20 | 1195.2 | 264 | 30 | 412.8054 | 450 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 365.174 | 300MCM | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 20.88 | 71245.525 | 40 | 55 | 20 | 2939.904 | 29.399 | 14.6995 | 1200 | 38 | 70 | 28 | 71.5556 | 69903.8583
Specs: | [6 empty] | Transformer Sizing (3 phase) |  | (Iac): Circuit Breaker Sizing | Wire Sizing | [8 empty] | Heat Dissipation |  | Environment |  | Fan Sizing |  |  |  | Air Conditionner Sizing
Vnom |  | Output |  | Input |  |  |  |  | (Iac): Primary Input; DC: Secondary Output; Scale: DC Output | Primary |  |  | Secondary |  |  | DC Output |  |  |  |  | Ambient T | Inside T |  |  | Fan CFM | Fan CFM | Encl.Size
240 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec | 30 | Amps | CB | 30 | Amps | CB | 30 |  | Amps | 15 | Amps | Gage | 10 | Amps | Gage | 10 | Amps | Gage |  |  | 40 | 55 | 20 | Required | 100 | 200 | Model: | W | H | Depth | Surface | Required
#cel | (V) | (V) | (A) | (V) | (A) | 12 | (Vac) | (Vac) | 20 | (Iac) | (Kva) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (A) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | Safety % | (A) | (AWG) | (kW) | (BTU) | (deg C) | (deg C) | Safety % | (CFM) | QTY | QTY | ARM | (in) | (in) | (in) | (ft²) | (BTU)
120 | 2.45 | 294 | 5 | 120 | 10.8253 | 12 | 140.9318 | 244.1011 | 20 | 4.98 | 2.25 | 30 | 14.0729 | 15 | 30 | 6.474 | 10 | 30 | 6.5 | 10 | 15 | 12.4491 | #10 | 10 | 5.478 | #10 | 10 | 5.5 | #10 | 0.1675 | 571.5338 | 40 | 55 | 20 | 23.584 | 0.23584 | 0.11792 | 450 | 24 | 30 | 16 | 19.3333 | 209.0338
120 | 2.45 | 294 | 10 | 120 | 20.4478 | 12 | 140.9318 | 244.1011 | 20 | 9.96 | 4.25 | 30 | 26.5822 | 30 | 30 | 12.948 | 15 | 30 | 13 | 15 | 15 | 23.515 | #10 | 10 | 10.956 | #10 | 10 | 11 | #10 | 0.3175 | 1083.3551 | 40 | 55 | 20 | 44.704 | 0.44704 | 0.22352 | 450 | 24 | 30 | 16 | 19.3333 | 720.8551
120 | 2.45 | 294 | 15 | 120 | 31.2731 | 12 | 140.9318 | 244.1011 | 20 | 14.94 | 6.5 | 30 | 40.6551 | 50 | 30 | 19.422 | 20 | 30 | 19.5 | 20 | 15 | 35.9641 | #10 | 10 | 16.434 | #10 | 10 | 16.5 | #10 | 0.485 | 1654.8889 | 40 | 55 | 20 | 68.288 | 0.68288 | 0.34144 | 600 | 24 | 48 | 16 | 29.3333 | 1104.8889
120 | 2.45 | 294 | 20 | 120 | 40.8956 | 12 | 140.9318 | 244.1011 | 20 | 19.92 | 8.5 | 30 | 53.1643 | 60 | 30 | 25.896 | 30 | 30 | 26 | 30 | 15 | 47.03 | #8 | 10 | 21.912 | #10 | 10 | 22 | #10 | 0.635 | 2166.7102 | 40 | 55 | 20 | 89.408 | 0.89408 | 0.44704 | 600 | 24 | 48 | 16 | 29.3333 | 1616.7102
120 | 2.45 | 294 | 25 | 208 | 30.5329 | 12 | 140.9318 | 244.1011 | 20 | 24.9 | 11 | 30 | 39.6928 | 40 | 30 | 32.37 | 40 | 30 | 32.5 | 40 | 15 | 35.1129 | #10 | 10 | 27.39 | #10 | 10 | 27.5 | #10 | 0.82 | 2797.9564 | 40 | 55 | 20 | 115.456 | 1.1546 | 0.57728 | 600 | 24 | 48 | 16 | 29.3333 | 2247.9564
120 | 2.45 | 294 | 30 | 208 | 36.0844 | 12 | 140.9318 | 244.1011 | 20 | 29.88 | 13 | 30 | 46.9097 | 50 | 30 | 38.844 | 40 | 30 | 39 | 40 | 15 | 41.4971 | #8 | 10 | 32.868 | #10 | 10 | 33 | #10 | 0.97 | 3309.7777 | 40 | 55 | 20 | 136.576 | 1.3658 | 0.68288 | 600 | 24 | 48 | 16 | 29.3333 | 2759.7777
120 | 2.45 | 294 | 35 | 208 | 41.6358 | 12 | 140.9318 | 244.1011 | 20 | 34.86 | 15 | 30 | 54.1266 | 60 | 30 | 45.318 | 50 | 30 | 45.5 | 50 | 15 | 47.8812 | #8 | 10 | 38.346 | #10 | 10 | 38.5 | #10 | 1.12 | 3821.599 | 40 | 55 | 20 | 157.696 | 1.577 | 0.78848 | 600 | 24 | 48 | 16 | 29.3333 | 3271.599
120 | 2.45 | 294 | 40 | 240 | 40.8956 | 12 | 140.9318 | 244.1011 | 20 | 39.84 | 17 | 30 | 53.1643 | 60 | 30 | 51.792 | 60 | 30 | 52 | 60 | 15 | 47.03 | #8 | 10 | 43.824 | #8 | 10 | 44 | #8 | 1.27 | 4333.4203 | 40 | 55 | 20 | 178.816 | 1.7882 | 0.89408 | 600 | 24 | 48 | 16 | 29.3333 | 3783.4203
120 | 2.45 | 294 | 50 | 480 | 26.4619 | 12 | 140.9318 | 244.1011 | 20 | 49.8 | 22 | 30 | 34.4005 | 40 | 30 | 64.74 | 70 | 30 | 65 | 70 | 15 | 30.4312 | #10 | 10 | 54.78 | #8 | 10 | 55 | #8 | 1.64 | 5595.9129 | 40 | 55 | 20 | 230.912 | 2.3091 | 1.1546 | 800 | 34 | 48 | 28 | 47.9444 | 4696.9545
120 | 2.45 | 294 | 60 | 480 | 31.2731 | 12 | 140.9318 | 244.1011 | 20 | 59.76 | 26 | 30 | 40.6551 | 50 | 30 | 77.688 | 80 | 30 | 78 | 80 | 15 | 35.9641 | #10 | 10 | 65.736 | #6 | 10 | 66 | #6 | 1.94 | 6619.5555 | 40 | 55 | 20 | 273.152 | 2.7315 | 1.3658 | 800 | 34 | 48 | 28 | 47.9444 | 5720.5971
120 | 2.45 | 294 | 75 | 480 | 38.49 | 12 | 140.9318 | 244.1011 | 20 | 74.7 | 32 | 30 | 50.037 | 50 | 30 | 97.11 | 100 | 30 | 97.5 | 100 | 15 | 44.2635 | #8 | 10 | 82.17 | #4 | 10 | 82.5 | #4 | 2.39 | 8155.0194 | 40 | 55 | 20 | 336.512 | 3.3651 | 1.6826 | 800 | 34 | 48 | 28 | 47.9444 | 7256.061
120 | 2.45 | 294 | 100 | 480 | 51.721 | 12 | 140.9318 | 244.1011 | 20 | 99.6 | 43 | 30 | 67.2373 | 70 | 30 | 129.48 | 150 | 30 | 130 | 150 | 15 | 59.4791 | #8 | 10 | 109.56 | #3 | 10 | 110 | #3 | 3.21 | 10952.9758 | 40 | 55 | 20 | 451.968 | 4.5197 | 2.2598 | 800 | 34 | 48 | 28 | 47.9444 | 10054.0175
120 | 2.45 | 294 | 125 | 480 | 63.7491 | 12 | 140.9318 | 244.1011 | 20 | 124.5 | 53 | 30 | 82.8738 | 90 | 30 | 161.85 | 175 | 30 | 162.5 | 175 | 15 | 73.3115 | #6 | 10 | 136.95 | #2 | 10 | 137.5 | #2 | 3.96 | 13512.0823 | 40 | 55 | 20 | 557.568 | 5.5757 | 2.7878 | 800 | 34 | 48 | 28 | 47.9444 | 12613.124
120 | 2.45 | 294 | 150 | 480 | 76.98 | 12 | 140.9318 | 244.1011 | 20 | 149.4 | 64 | 30 | 100.074 | 100 | 30 | 194.22 | 200 | 30 | 195 | 200 | 15 | 88.527 | #4 | 10 | 164.34 | #1 | 10 | 165 | #1 | 4.78 | 16310.0388 | 40 | 55 | 20 | 673.024 | 6.7302 | 3.3651 | 800 | 34 | 48 | 28 | 47.9444 | 15411.0804
120 | 2.45 | 294 | 175 | 480 | 89.0082 | 12 | 140.9318 | 244.1011 | 20 | 174.3 | 74 | 30 | 115.7106 | 125 | 30 | 226.59 | 250 | 30 | 227.5 | 250 | 15 | 102.3594 | #4 | 10 | 191.73 | #1/0 | 10 | 192.5 | #1/0 | 5.53 | 18869.1453 | 40 | 55 | 20 | 778.624 | 7.7862 | 3.8931 | 1200 | 38 | 70 | 28 | 71.5556 | 17527.4786
120 | 2.45 | 294 | 200 | 480 | 102.2391 | 12 | 140.9318 | 244.1011 | 20 | 199.2 | 85 | 30 | 132.9108 | 150 | 30 | 258.96 | 300 | 30 | 260 | 300 | 15 | 117.575 | #3 | 10 | 219.12 | #2/0 | 10 | 220 | #2/0 | 6.35 | 21667.1017 | 40 | 55 | 20 | 894.08 | 8.9408 | 4.4704 | 1200 | 38 | 70 | 28 | 71.5556 | 20325.435
120 | 2.45 | 294 | 250 | 480 | 127.4982 | 12 | 140.9318 | 244.1011 | 20 | 249 | 106 | 30 | 165.7476 | 175 | 30 | 323.7 | 350 | 30 | 325 | 350 | 15 | 146.6229 | #1 | 10 | 273.9 | #4/0 | 10 | 275 | #4/0 | 7.92 | 27024.1646 | 40 | 55 | 20 | 1115.136 | 11.1514 | 5.5757 | 1200 | 38 | 70 | 28 | 71.5556 | 25682.498
120 | 2.45 | 294 | 300 | 480 | 152.7573 | 12 | 140.9318 | 244.1011 | 20 | 298.8 | 127 | 30 | 198.5844 | 200 | 30 | 388.44 | 400 | 30 | 390 | 400 | 15 | 175.6708 | #1/0 | 10 | 328.68 | 250MCM | 10 | 330 | 250MCM | 9.49 | 32381.2276 | 40 | 55 | 20 | 1336.192 | 13.3619 | 6.681 | 1200 | 38 | 70 | 28 | 71.5556 | 31039.5609
120 | 2.45 | 294 | 350 | 480 | 178.0163 | 12 | 140.9318 | 244.1011 | 20 | 348.6 | 148 | 30 | 231.4212 | 250 | 30 | 453.18 | 500 | 30 | 455 | 500 | 15 | 204.7188 | #2/0 | 10 | 383.46 | #2/0 2x | 10 | 385 | #2/0 2x | 11.06 | 37738.2905 | 40 | 55 | 20 | 1557.248 | 15.5725 | 7.7862 | 1200 | 38 | 70 | 28 | 71.5556 | 36396.6239
120 | 2.45 | 294 | 400 | 480 | 203.2754 | 12 | 140.9318 | 244.1011 | 20 | 398.4 | 169 | 30 | 264.258 | 300 | 30 | 517.92 | 600 | 30 | 520 | 600 | 15 | 233.7667 | #3/0 | 10 | 438.24 | #3/0 2x | 10 | 440 | #3/0 2x | 12.63 | 43095.3535 | 40 | 55 | 20 | 1778.304 | 17.783 | 8.8915 | 1200 | 38 | 70 | 28 | 71.5556 | 41753.6868
120 | 2.45 | 294 | 450 | 480 | 228.5345 | 12 | 140.9318 | 244.1011 | 20 | 448.2 | 190 | 30 | 297.0948 | 300 | 30 | 582.66 | 600 | 30 | 585 | 600 | 15 | 262.8147 | #4/0 | 10 | 493.02 | #3/0 2x | 10 | 495 | #3/0 2x | 14.2 | 48452.4164 | 40 | 55 | 20 | 1999.36 | 19.9936 | 9.9968 | 1200 | 38 | 70 | 28 | 71.5556 | 47110.7497
120 | 2.45 | 294 | 500 | 480 | 253.7936 | 12 | 140.9318 | 244.1011 | 20 | 498 | 211 | 30 | 329.9316 | 350 | 30 | 647.4 | 700 | 30 | 650 | 700 | 15 | 291.8626 | #4/0 | 10 | 547.8 | #4/0 2x | 10 | 550 | #4/0 2x | 15.77 | 53809.4793 | 40 | 55 | 20 | 2220.416 | 22.2042 | 11.1021 | 1200 | 38 | 70 | 28 | 71.5556 | 52467.8127
120 | 2.45 | 294 | 600 | 480 | 304.3117 | 12 | 140.9318 | 244.1011 | 20 | 597.6 | 253 | 30 | 395.6052 | 400 | 30 | 776.88 | 800 | 30 | 780 | 800 | 15 | 349.9585 | 300MCM | 10 | 657.36 | 300MCM 2x | 10 | 660 | 300MCM 2x | 18.91 | 64523.6052 | 40 | 55 | 20 | 2662.528 | 26.6253 | 13.3126 | 1200 | 38 | 70 | 28 | 71.5556 | 63181.9386
120 | 2.45 | 294 | 700 | 480 | 354.8299 | 12 | 140.9318 | 244.1011 | 20 | 697.2 | 295 | 30 | 461.2788 | 500 | 30 | 906.36 | 1000 | 30 | 910 | 1000 | 15 | 408.0543 | #2/0 2x | 10 | 766.92 | Buss | 10 | 770 | Buss | 22.05 | 75237.7311 | 40 | 55 | 20 | 3104.64 | 31.0464 | 15.5232 | 1200 | 38 | 70 | 28 | 71.5556 | 73896.0644
120 | 2.45 | 294 | 800 | 480 | 405.348 | 12 | 140.9318 | 244.1011 | 20 | 796.8 | 337 | 30 | 526.9524 | 600 | 30 | 1035.84 | 1200 | 30 | 1040 | 1200 | 15 | 466.1502 | #3/0 2x | 10 | 876.48 | Buss | 10 | 880 | Buss | 25.19 | 85951.857 | 40 | 55 | 20 | 3546.752 | 35.4675 | 17.7338 | 1200 | 38 | 70 | 28 | 71.5556 | 84610.1903
120 | 2.45 | 294 | 900 | 480 | 455.8662 | 12 | 140.9318 | 244.1011 | 20 | 896.4 | 379 | 30 | 592.626 | 600 | 30 | 1165.32 | 1200 | 30 | 1170 | 1200 | 15 | 524.2461 | #4/0 2x | 10 | 986.04 | Buss | 10 | 990 | Buss | 28.33 | 96665.9829 | 40 | 55 | 20 | 3988.864 | 39.8886 | 19.9443 | 1200 | 38 | 70 | 28 | 71.5556 | 95324.3162
120 | 2.45 | 294 | 1000 | 480 | 507.5871 | 12 | 140.9318 | 244.1011 | 20 | 996 | 422 | 30 | 659.8632 | 700 | 30 | 1294.8 | Check | 30 | 1300 | Check | 15 | 583.7252 | 250MCM 2x | 10 | 1095.6 | Buss | 10 | 1100 | Buss | 31.54 | 107618.9587 | 40 | 55 | 20 | 4440.832 | 44.4083 | 22.2042 | 1200 | 38 | 70 | 28 | 71.5556 | 106277.292
120 | 2.45 | 294 | 1100 | 480 | 558.1053 | 12 | 140.9318 | 244.1011 | 20 | 1095.6 | 464 | 30 | 725.5368 | 800 | 30 | 1424.28 | Check | 30 | 1430 | Check | 15 | 641.821 | 250MCM 2x | 10 | 1205.16 | Buss | 10 | 1210 | Buss | 34.68 | 118333.0846 | 40 | 55 | 20 | 4882.944 | 48.8294 | 24.4147 | 1200 | 38 | 70 | 28 | 71.5556 | 116991.4179
120 | 2.45 | 294 | 1200 | 480 | 608.6234 | 12 | 140.9318 | 244.1011 | 20 | 1195.2 | 506 | 30 | 791.2104 | 800 | 30 | 1553.76 | Check | 30 | 1560 | Check | 15 | 699.9169 | 300MCM 2x | 10 | 1314.72 | Buss | 10 | 1320 | Buss | 37.82 | 129047.2104 | 40 | 55 | 20 | 5325.056 | 53.2506 | 26.6253 | 1200 | 38 | 70 | 28 | 71.5556 | 127705.5438
120 | 2.45 | 294 | 2000 | 480 | 1013.9714 | 12 | 140.9318 | 244.1011 | 20 | 1992 | 843 | 30 | 1318.1628 | Check | 30 | 2589.6 | Check | 30 | 2600 | Check | 15 | 1166.0671 | Buss | 10 | 2191.2 | Buss | 10 | 2200 | Buss | 63.01 | 214999.0674 | 40 | 55 | 20 | 8871.808 | 88.7181 | 44.359 | 1200 | 38 | 70 | 28 | 71.5556 | 213657.4008

## HS250-DATA
Natural Cooling |  | 1Mod
Length | Length | Rθha | UNIT PRICE MAY 2009
(mm) | (") | (°C/W)
165 | 6.4961 | 0.369 | 16.35
250 | 9.8425 | 0.28 | 19.86
330 | 12.9921 | 0.255 | 24.55
380 | 14.9606 | 0.25 | 28.26
3Mod
Length | Length | Rθha
(mm) | (") | (°C/W)
165 | 6.4961 | 0.33
250 | 9.8425 | 0.241
330 | 12.9921 | 0.22
380 | 14.9606 | 0.21
forced Cooling |  | 1Mod
Length | Length | Rθha | UNIT PRICE MAY 2009
(mm) | (") | (°C/W) |  | HS250-AD | Fan | TOTAL
165 | 6.4961 | 0.122 | 16.35 | 1.83 | 10 | 28.18
250 | 9.8425 | 0.115 | 19.86 | 1.83 | 10 | 31.69
330 | 12.9921 | 0.11 | 24.55 | 1.83 | 10 | 36.38
380 | 14.9606 | 0.106 | 28.26 | 1.83 | 10 | 40.09
3Mod
Length | Length | Rθha
(mm) | (") | (°C/W)
165 | 6.4961 | 0.114
250 | 9.8425 | 0.099
330 | 12.9921 | 0.084
380 | 14.9606 | 0.072

## HS250-TEST
3Φ-1Φ-DC
Circuit Type | Total number of devices = n | Number of devices/HS= ns | Number of HS | Idc | Ts | Ta | Idave | F Idrms/Idave | Device Part No | Idave Max | Idrms Max | Ifsm | Tjmax | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | Pd | Pt/HS =nsxPd | Pt =nxPd | HS250 Length | FAN | Deduction Rθsa | Tj | Ts | Ta | Tj
|  |  |  | (A) | (°C) | (°C) | (A) |  |  | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W) | (W) | (W) | (W) | (") | Y/N | (°C/W) | (°C) | (°C) | (°C) | (°C)
3 | 6 | 6 | 1 | 160 | 70 | 34.6 | 53.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 58.1333 | 348.8 | 348.8 |  |  | 0.10149 | 85.696 |  |  | 85.696
3 | 6 | 6 | 1 | 160 | 77 | 23 | 53.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 58.1333 | 348.8 | 348.8 |  |  | 0.15482 | 92.696 |  |  | 92.696
bd | 1 | 1 | 1 | 160 |  |  | 160 | 1 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 174.4 | 174.4 | 174.4 |  |  | 0 | 47.088 |  |  | 47.088
3 | 6 | 6 | 1 | 127 | 97.6 | 0 | 42.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 44.0478 | 264.287 | 264.287 |  |  | 0.3693 | 109.4929 |  |  | 109.4929
3 | 6 | 6 | 1 | 160 | 70 | 34.6 | 53.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 58.1333 | 348.8 | 348.8 |  |  | 0.10149 | 85.696 |  |  | 85.696
3 | 6 | 6 | 1 | 160 | 70 | 34.6 | 53.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 58.1333 | 348.8 | 348.8 |  |  | 0.10149 | 85.696 |  |  | 85.696
3 | 6 | 6 | 1 | 325 | 81.3 | 34.6 | 108.3333 | 1.7321 | ND431225 |  |  |  | 130 | 0.819 | 0.589 | 0.14 | 0.06 | 109.4627 | 656.7762 | 656.7762 |  |  | 0.071105 | 103.1925 |  |  | 103.1925
bd | 1 | 1 | 1 | 325 | 69.7 | 34.6 | 325 | 1 | LS411260 |  |  |  | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 268.4419 | 268.4419 | 268.4419 |  |  | 0.13075 | 92.5176 |  |  | 92.5176
3 | 6 | 6 | 1 | 352 | 83.4 | 32.3 | 117.3333 | 1.7321 | ND431225 |  |  |  | 130 | 0.819 | 0.589 | 0.14 | 0.06 | 120.4225 | 722.5349 | 722.5349 |  |  | 0.070723 | 107.4845 |  |  | 107.4845
bd | 1 | 1 | 1 | 352 | 70.6 | 32.3 | 352 | 1 | LS411260 |  |  |  | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 293.0527 | 293.0527 | 293.0527 |  |  | 0.13069 | 95.5095 |  |  | 95.5095
3 | 6 | 6 | 1 | 375 | 90.4 | 34.5 | 125 | 1.7321 | ND431225 |  |  |  | 130 | 0.819 | 0.589 | 0.14 | 0.06 | 129.9844 | 779.9062 | 779.9062 |  |  | 0.071675 | 116.3969 |  |  | 116.3969
bd | 1 | 1 | 1 | 375 | 75.1 | 34.5 | 375 | 1 | LS411260 |  |  |  | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 314.2969 | 314.2969 | 314.2969 |  |  | 0.12918 | 101.8152 |  |  | 101.8152
3 | 6 | 6 | 1 | 115 | 90.8 | 35.2 | 38.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 39.1958 | 235.175 | 235.175 |  |  | 0.23642 | 101.3829 |  |  | 101.3829
3 | 6 | 6 | 1 | 127 | 97.6 | 37.3 | 42.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 44.0478 | 264.287 | 264.287 |  |  | 0.22816 | 109.4929 |  |  | 109.4929
3 | 6 | 6 | 1 | 106 | 92.3 | 31.5 | 35.3333 | 1.7321 | CD63xx15B |  |  |  | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 35.6513 | 213.908 | 213.908 |  |  | 0.28423 | 101.9259 |  |  | 101.9259
bd | 1 | 1 | 1 | 106 | 95.8 | 31.5 | 106 | 1 | LS411260 |  |  |  | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 81.9123 | 81.9123 | 81.9123 |  |  | 0.78499 | 102.7625 |  |  | 102.7625
3 | 6 | 6 | 1 | 56 | 78.3 | 37 | 18.6667 | 1.7321 | EFG |  |  |  | 125 | 1.55 | 0 | 0.3 | 0.05 | 28.9333 | 173.6 | 173.6 |  |  | 0.2379 | 88.4267 |  |  | 88.4267
bd | 1 | 1 | 1 | 56 | 78.3 | 37 | 56 | 1 | F18 |  |  |  | 125 | 1.4 | 0 | 0.28 | 0.02 | 78.4 | 78.4 | 78.4 |  |  | 0.52679 | 101.82 |  |  | 101.82
3 | 6 | 6 | 1 | 55 | 77.1 | 40.7 | 18.3333 | 1.7321 | EFG |  |  |  | 125 | 0.85 | 1.8 | 0.3 | 0.05 | 17.3983 | 104.39 | 104.39 |  |  | 0.34869 | 83.1894 |  |  | 83.1894
3 | 6 | 6 | 1 | 51 | 72.6 | 38.9 | 17 | 1.7321 | EFG |  |  |  | 125 | 0.85 | 1.8 | 0.3 | 0.05 | 16.0106 | 96.0636 | 96.0636 |  |  | 0.35081 | 78.2037 |  |  | 78.2037
bd | 1 | 1 | 1 | 56 | 78.3 | 37 | 56 | 1 | F18 |  |  |  | 125 | 0.85 | 1.8 | 0.28 | 0.02 | 53.2448 | 53.2448 | 53.2448 |  |  | 0.77566 | 94.2734 |  |  | 94.2734
3 | 6 | 6 | 1 | 56 | 90 | 37 | 18.6667 | 1.7321 | SK 70 DT |  |  |  | 125 | 1 | 10 | 1.2 | 0 | 29.12 | 174.72 | 174.72 |  |  | 0.30334 | 124.944 |  |  | 124.944
3 | 6 | 6 | 1 | 100 | 85.3 | 34.5 | 33.3333 | 1.7321 | EFG |  |  |  | 125 | 1 | 0 | 0.3 | 0.05 | 33.3333 | 200 | 200 |  |  | 0.254 | 96.9667 |  |  | 96.9667
bd | 1 | 1 | 1 | 149 | 72.7 | 34.2 | 149 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 153.2912 | 153.2912 | 153.2912 |  |  | 0.25116 | 115.6215 |  |  | 115.6215
bd | 1 | 1 | 1 | 149 | 75.6 | 34.2 | 149 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 153.2912 | 153.2912 | 153.2912 |  |  | 0.27007 | 118.5215 |  |  | 118.5215
bd | 1 | 1 | 1 | 149 | 80.2 | 34.2 | 149 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 153.2912 | 153.2912 | 153.2912 |  |  | 0.30008 | 123.1215 |  |  | 123.1215
bd | 1 | 1 | 1 | 149 | 90.8 | 34.2 | 149 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 153.2912 | 153.2912 | 153.2912 |  |  | 0.36923 | 133.7215 |  |  | 133.7215
bd | 1 | 1 | 1 | 181 | 86.3 | 38.1 | 181 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 193.1632 | 193.1632 | 193.1632 |  |  | 0.24953 | 140.3857 |  |  | 140.3857
bd | 1 | 1 | 1 | 181 | 87.1 | 38.1 | 181 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 193.1632 | 193.1632 | 193.1632 |  |  | 0.25367 | 141.1857 |  |  | 141.1857
bd | 1 | 1 | 1 | 181 | 89.9 | 38.1 | 181 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 193.1632 | 193.1632 | 193.1632 |  |  | 0.26817 | 143.9857 |  |  | 143.9857
bd | 1 | 1 | 1 | 181 | n/a | 38.1 | 181 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 193.1632 | 193.1632 | 193.1632 |  |  | #VALUE! | #VALUE! |  |  | #VALUE!
bd | 1 | 1 | 1 | 176 | 60 | 39.7 | 176 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 186.7712 | 186.7712 | 186.7712 |  |  | 0.10869 | 112.2959 |  |  | 112.2959
bd | 1 | 1 | 1 | 176 | 60.8 | 39.7 | 176 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 186.7712 | 186.7712 | 186.7712 |  |  | 0.11297 | 113.0959 |  |  | 113.0959
bd | 1 | 1 | 1 | 176 | 62.1 | 39.7 | 176 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 186.7712 | 186.7712 | 186.7712 |  |  | 0.11993 | 114.3959 |  |  | 114.3959
bd | 1 | 1 | 1 | 176 | 62.8 | 39.7 | 176 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 186.7712 | 186.7712 | 186.7712 |  |  | 0.12368 | 115.0959 |  |  | 115.0959
bd | 1 | 1 | 1 | 201 | 63 | 39.3 | 201 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 219.3312 | 219.3312 | 219.3312 |  |  | 0.10806 | 124.4127 |  |  | 124.4127
bd | 1 | 1 | 1 | 201 | 63.9 | 39.3 | 201 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 219.3312 | 219.3312 | 219.3312 |  |  | 0.11216 | 125.3127 |  |  | 125.3127
bd | 1 | 1 | 1 | 201 | 65.3 | 39.3 | 201 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 219.3312 | 219.3312 | 219.3312 |  |  | 0.11854 | 126.7127 |  |  | 126.7127
bd | 1 | 1 | 1 | 201 | 66.5 | 39.3 | 201 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 219.3312 | 219.3312 | 219.3312 |  |  | 0.12401 | 127.9127 |  |  | 127.9127
bd | 1 | 1 | 1 | 225 | 66 | 38.8 | 225 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 252 | 252 | 252 |  |  | 0.10794 | 136.56 |  |  | 136.56
bd | 1 | 1 | 1 | 225 | 66.9 | 38.8 | 225 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 252 | 252 | 252 |  |  | 0.11151 | 137.46 |  |  | 137.46
bd | 1 | 1 | 1 | 225 | 68.3 | 38.8 | 225 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 252 | 252 | 252 |  |  | 0.11706 | 138.86 |  |  | 138.86
bd | 1 | 1 | 1 | 225 | 70.1 | 38.8 | 225 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 252 | 252 | 252 |  |  | 0.12421 | 140.66 |  |  | 140.66
bd | 1 | 1 | 1 | 256 | 70.3 | 39.1 | 256 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 296.2432 | 296.2432 | 296.2432 |  |  | 0.10532 | 153.2481 |  |  | 153.2481
bd | 1 | 1 | 1 | 256 | 71.2 | 39.1 | 256 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 296.2432 | 296.2432 | 296.2432 |  |  | 0.10836 | 154.1481 |  |  | 154.1481
bd | 1 | 1 | 1 | 256 | 73 | 39.1 | 256 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 296.2432 | 296.2432 | 296.2432 |  |  | 0.11443 | 155.9481 |  |  | 155.9481
bd | 1 | 1 | 1 | 256 | 75.3 | 39.1 | 256 | 1 | CD63xx15B |  |  |  | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 296.2432 | 296.2432 | 296.2432 |  |  | 0.1222 | 158.2481 |  |  | 158.2481
3 | 6 | 6 | 1 | 300 | 84 | 49 | 100 | 1.7321 | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 75 | 450 | 450 |  |  | 0.077778 | 99 |  |  | 99
3 | 6 | 6 | 1 | 295 | 98 | 46.5 | 98.3333 | 1.7321 | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 118.3933 | 710.36 | 710.36 |  |  | 0.072498 | 131.1501 |  |  | 131.1501
3 | 6 | 6 | 1 | 275 | 94 | 45 | 91.6667 | 1.7321 | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 108.1667 | 649 | 649 |  |  | 0.075501 | 124.2867 |  |  | 124.2867
3 | 6 | 6 | 1 | 170 | 95 | 33 | 56.6667 | 1.7321 | CD61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 59.7267 | 358.36 | 358.36 |  |  | 0.17301 | 111.7235 |  |  | 111.7235
3 | 6 | 6 | 1 | 150 | 95 | 33 | 50 | 1.7321 | CD61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 51.5 | 309 | 309 |  |  | 0.20065 | 109.42 |  |  | 109.42
3 | 6 | 6 | 1 | 170 | 97 | 31 | 56.6667 | 1.7321 | CD61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 59.7267 | 358.36 | 358.36 |  |  | 0.18417 | 113.7235 |  |  | 113.7235
3 | 6 | 6 | 1 | 150 | 92 | 33.2 | 50 | 1.7321 | CD61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 51.5 | 309 | 309 |  |  | 0.19029 | 106.42 |  |  | 106.42
BD | 1 | 1 | 1 | 350 | 86.5 | 54 | 350 | 1 | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 268.1 | 268.1 | 268.1 |  |  | 0.12122 | 140.12 |  |  | 140.12
BD | 1 | 1 | 1 | 400 | 94 | 54 | 400 | 1 | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 312.8 | 312.8 | 312.8 |  |  | 0.12788 | 156.56 |  |  | 156.56
3 | 6 | 6 | 1 | 350 | 98.6 | 54.1 | 116.6667 | 1.7321 | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 89.3667 | 536.2 | 536.2 |  |  | 0.082991 | 116.4733 |  |  | 116.4733
3 | 6 | 6 | 1 | 400 | 107.3 | 58.2 | 133.3333 | 1.7321 | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 104.2667 | 625.6 | 625.6 |  |  | 0.078485 | 128.1533 |  |  | 128.1533
[9 empty] | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | [5 empty] | 0.024667
[10 empty] | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W)
[9 empty] | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2
[9 empty] | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1
[9 empty] | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06
Circuit Type | Total number of devices = n | Number of devices/HS= ns | Number of HS | Idc | Ts | Ta | Idave | F Idrms/Idave | Device Part No | Idave Max | Idrms Max | Ifsm | Tjmax | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | Pd | Pt/HS =nsxPd | Pt =nxPd | HS250 Length | FAN | Deduction Rθsa | Tj | Ts | Ta | Tj
|  |  |  | (A) | (°C) | (°C) | (A) |  |  | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W) | (W) | (W) | (W) | (") | Y/N | (°C/W) | (°C) | (°C) | (°C) | (°C)
3 | 6 | 2 | 1 | 500 | 73 | 23 | 166.6667 | 1.7321 | ND431225 |  |  |  | 130 | 0.819 | 0.589 | 0.14 | 0.06 | 185.5833 | 371.1667 | 1113.5 |  |  | 0.13471 | 110.1167 |  |  | 110.1167
BD | 1 | 1 | 1 | 500 | 86 | 23 | 500 | 1 | LS411260 |  |  |  | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 434.25 | 434.25 | 434.25 |  |  | 0.14508 | 122.9112 |  |  | 122.9112

## FUSE DATA
FUSES
Type | FA | UF | TD | FA | FA | UF | UF | FA | FA | TD | FA | [10 empty] | Type | UF
AC rating (V) | 600 | 600 | 600 | 600 | 600 | 300 | 700 | 300 | 600 | 600 | 600 | 600 | [9 empty] | AC rating (V) | 300
DC rating (V) | 500 | 600 | 500 | 300 | 500 | 300 | 650 | 160 | 300 | 500 | 340 | 300 | [9 empty] | DC rating (V) | 300
[9 empty] | Ferraz | Ferraz | Edison
Fuse rating | ATM | A60Q | AJT | A4J | HSJ | A30QS | A70P | A3T | A6T | A4BQ | LCU | KRP | [9 empty] | Fuse rating | A30QS
(A) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | (A/10ms) | # cap de 10000uF | 1.75 | 1.8 | 1.85 | 1.9 | 1.95 | 2 | 2.05 | 2.1 | (A) | (A/10ms)
5 | 70 | 60 | 120 | 80 | 0 | 0 | 0 | 30 | 45 |  |  |  | 0 | [8 empty] | 40 | 180
10 | 150 | 70 | 190 | 150 | 0 | 0 | 0 | 60 | 100 |  |  |  | 0 | [8 empty] | 50 | 235
15 | 250 | 110 | 250 | 130 | 83 | 0 | 0 | 88 | 145 |  |  |  | 0 | [8 empty] | 60 | 269
20 | 300 | 130 | 300 | 180 | 130 | 0 | 0 | 115 | 225 |  |  |  | 0 | [8 empty] | 70 | 260
25 | 350 | 180 | 370 | 250 | 150 | 0 | 0 | 150 | 275 |  |  |  | 0 | [8 empty] | 80 | 349
30 | 400 | 225 | 490 | 300 | 230 | 0 | 0 | 175 | 340 |  |  |  | 0 | [8 empty] | 90 | 391
40 | 0 | 0 | 700 | 537 | 325 | 180 | 200 | 275 | 500 |  |  | 1.8056 | 1.2857 | 22.8571 | 22.2222 | 21.6216 | 21.0526 | 20.5128 | 20 | 19.5122 | 19.0476 | 100 | 461
50 | 0 | 0 | 800 | 671 | 400 | 235 | 250 | 345 | 625 |  |  | 1.7021 | 1.6786 | 28.5714 | 27.7778 | 27.027 | 26.3158 | 25.641 | 25 | 24.3902 | 23.8095 | 125 | 510
60 | 0 | 0 | 900 | 800 | 500 | 269 | 300 | 400 | 750 |  |  | 1.8587 | 1.9214 | 34.2857 | 33.3333 | 32.4324 | 31.5789 | 30.7692 | 30 | 29.2683 | 28.5714 | 150 | 700
70 | 0 | 0 | 1000 | 670 | 600 | 260 | 300 | 530 | 1000 |  |  | 2.3077 | 1.8571 | 40 | 38.8889 | 37.8378 | 36.8421 | 35.8974 | 35 | 34.1463 | 33.3333 | 175 | 775
80 | 0 | 0 | 1100 | 765 | 700 | 349 | 450 | 615 | 1200 |  |  | 2.0057 | 2.4929 | 45.7143 | 44.4444 | 43.2432 | 42.1053 | 41.0256 | 40 | 39.0244 | 38.0952 | 200 | 949
90 | 0 | 0 | 1200 | 861 | 830 | 391 | 520 | 690 | 1300 |  |  | 2.1228 | 2.7929 | 51.4286 | 50 | 48.6486 | 47.3684 | 46.1538 | 45 | 43.9024 | 42.8571 | 225 | 860
100 | 0 | 0 | 1500 | 1000 | 920 | 461 | 600 | 760 | 1500 | 1300 |  | 1.9957 | 3.2929 | 57.1429 | 55.5556 | 54.0541 | 52.6316 | 51.2821 | 50 | 48.7805 | 47.619 | 250 | 1058
125 | 0 | 0 | 1750 | 1261 | 1150 | 510 | 740 | 900 | 1900 |  |  | 2.2549 | 3.6429 | 71.4286 | 69.4444 | 67.5676 | 65.7895 | 64.1026 | 62.5 | 60.9756 | 59.5238 | 275 | 1196
150 | 0 | 0 | 2200 | 1513 | 1300 | 700 | 900 | 1000 | 2300 | 1800 |  | 1.8571 | 5 | 85.7143 | 83.3333 | 81.0811 | 78.9474 | 76.9231 | 75 | 73.1707 | 71.4286 | 300 | 1324
175 | 0 | 0 | 2470 | 1775 | 1750 | 775 |  | 1200 | 2750 |  |  | 2.2581 | 5.5357 | 100 | 97.2222 | 94.5946 | 92.1053 | 89.7436 | 87.5 | 85.3659 | 83.3333 | 350 | 1724
200 | 0 | 0 | 2750 | 2000 | 2000 | 949 | 1250 | 1300 | 3000 | 2200 |  | 2.1075 | 6.7786 | 114.2857 | 111.1111 | 108.1081 | 105.2632 | 102.5641 | 100 | 97.561 | 95.2381 | 400 | 1984
225 | 0 | 0 | 3000 | 2700 | 2300 | 860 | 1300 | 1500 | 3600 |  |  | 2.6744 | 6.1429 | 128.5714 | 125 | 121.6216 | 118.4211 | 115.3846 | 112.5 | 109.7561 | 107.1429 | 450 | 2578
250 | 0 | 0 | 3250 | 3000 | 2500 | 1058 | 1500 | 1650 | 4250 | 2800 |  | 2.3629 | 7.5571 | 142.8571 | 138.8889 | 135.1351 | 131.5789 | 128.2051 | 125 | 121.9512 | 119.0476 | 500 | 2839
FUSES Type: 275; FUSES UF: 1196 |  | 8.5429 | 157.1429 | 152.7778 | 148.6486 | 144.7368 | 141.0256 | 137.5 | 134.1463 | 130.9524 | 550 | 3110
300 | 0 | 0 | 4000 | 3600 | 3200 | 1324 | 1750 | 2000 | 4900 | 4000 |  | 2.4169 | 9.4571 | 171.4286 | 166.6667 | 162.1622 | 157.8947 | 153.8462 | 150 | 146.3415 | 142.8571 | 600 | 3532
350 |  |  | 4750 | 4250 | 3600 | 1724 |  | 2350 | 5900 | 4800 |  | 2.0882 | 12.3143 | 200 | 194.4444 | 189.1892 | 184.2105 | 179.4872 | 175 | 170.7317 | 166.6667 | 700 | 3677
400 | 0 | 0 | 5250 | 4621 | 4500 | 1984 | 2500 | 2625 | 6500 | 5300 |  | 2.2681 | 14.1714 | 228.5714 | 222.2222 | 216.2162 | 210.5263 | 205.1282 | 200 | 195.122 | 190.4762 | 800 | 4196
450 | 0 | 0 | 7600 | 5000 | 5250 | 2578 | 2700 | 3400 | 7800 | 6100 |  | 2.0365 | 18.4143 | 257.1429 | 250 | 243.2432 | 236.8421 | 230.7692 | 225 | 219.5122 | 214.2857 | 900 | 4708
515 | 0 | 0 | 8500 | 5850 | 5800 | 2839 | 3000 | 3800 | 8900 | 6800 |  | 2.043 | 20.2786 | 294.2857 | 286.1111 | 278.3784 | 271.0526 | 264.1026 | 257.5 | 251.2195 | 245.2381 | 1000 | 5564
FUSES Type: 550; FUSES UF: 3110 |  | 22.2143 | 314.2857 | 305.5556 | 297.2973 | 289.4737 | 282.0513 | 275 | 268.2927 | 261.9048 | 1200 | 7286
600 | 0 | 0 | 10000 | 7000 | 6900 | 3532 | 3500 | 4600 | 10000 | 8000 |  | 1.9536 | 25.2286 | 342.8571 | 333.3333 | 324.3243 | 315.7895 | 307.6923 | 300 | 292.6829 | 285.7143 | 1500 | 10000
700 | 0 | 0 | 0 | 0 | 0 | 3677 |  | 5450 | 13000 | 9262 |  |  | 26.2643 | 400 | 388.8889 | 378.3784 | 368.4211 | 358.9744 | 350 | 341.4634 | 333.3333 | 1600 | 10900
FUSES Type: 750; FUSES TD: 9890 |  |  | 428.5714 | 416.6667 | 405.4054 | 394.7368 | 384.6154 | 375 | 365.8537 | 357.1429 | 1800 | 11777
800 | 0 | 0 | 0 | 0 | 0 | 4196 | 5000 | 6500 | 15000 | 10516 |  |  | 29.9714 | 457.1429 | 444.4444 | 432.4324 | 421.0526 | 410.2564 | 400 | 390.2439 | 380.9524 | 2000 | 13464
FUSES Type: 900; FUSES UF: 4708; FUSES TD: 11761 |  | 33.6286 | 514.2857 | 500 | 486.4865 | 473.6842 | 461.5385 | 450 | 439.0244 | 428.5714 | 2500 | 16826
1000 | 0 | 0 | 0 | 0 | 0 | 5564 | 7000 | 8000 | 0 | 13000 |  |  | 39.7429 | 571.4286 | 555.5556 | 540.5405 | 526.3158 | 512.8205 | 500 | 487.8049 | 476.1905 | 3000 | 19339
1200 | 0 | 0 | 0 | 0 | 0 | 7286 | 8800 | 9800 | 0 | 16000 |  |  | 52.0429 | 685.7143 | 666.6667 | 648.6486 | 631.5789 | 615.3846 | 600 | 585.3659 | 571.4286 | 3500 | 23280
FUSES Type: 1350; FUSES TD: 17884 |  |  | 771.4286 | 750 | 729.7297 | 710.5263 | 692.3077 | 675 | 658.5366 | 642.8571 | 4000 | 26068
1400 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 0 | 18510 |  |  |  | 800 | 777.7778 | 756.7568 | 736.8421 | 717.9487 | 700 | 682.9268 | 666.6667 | 4500 | 29407
1500 | 0 | 0 | 0 | 0 | 0 | 10000 | 10500 | 0 | 0 | 19757 |  |  | 71.4286 | 857.1429 | 833.3333 | 810.8108 | 789.4737 | 769.2308 | 750 | 731.7073 | 714.2857 | 5000 | verify data
1600 | 0 | 0 | 0 | 0 | 0 | 10900 | 11000 | 0 | 0 | 21000 |  |  | 77.8571 | 914.2857 | 888.8889 | 864.8649 | 842.1053 | 820.5128 | 800 | 780.4878 | 761.9048
FUSES Type: 1800; FUSES UF: 11777; FUSES TD: 23121 |  | 84.1214 | 1028.5714 | 1000 | 972.973 | 947.3684 | 923.0769 | 900 | 878.0488 | 857.1429
2000 | 0 | 0 | 0 | 0 | 0 | 13464 | 14000 | 0 | 0 | 25200 |  |  | 96.1714 | 1142.8571 | 1111.1111 | 1081.0811 | 1052.6316 | 1025.641 | 1000 | 975.6098 | 952.381
FUSES Type: 2500; FUSES UF: 16826; FUSES TD: 33200 |  | 120.1857 | 1428.5714 | 1388.8889 | 1351.3514 | 1315.7895 | 1282.0513 | 1250 | 1219.5122 | 1190.4762
FUSES Type: 3000; FUSES UF: 19339; FUSES TD: 41000 |  | 138.1357 | 1714.2857 | 1666.6667 | 1621.6216 | 1578.9474 | 1538.4615 | 1500 | 1463.4146 | 1428.5714
FUSES Type: 3500; FUSES UF: 23280; FUSES TD: 49829 |  | 166.2857 | 2000 | 1944.4444 | 1891.8919 | 1842.1053 | 1794.8718 | 1750 | 1707.3171 | 1666.6667
FUSES Type: 4000; FUSES UF: 26068; FUSES TD: 59000 |  | 186.2 | 2285.7143 | 2222.2222 | 2162.1622 | 2105.2632 | 2051.2821 | 2000 | 1951.2195 | 1904.7619
FUSES Type: 4500; FUSES UF: 29407 |  | 210.05 | 2571.4286 | 2500 | 2432.4324 | 2368.4211 | 2307.6923 | 2250 | 2195.122 | 2142.8571
5000 | [5 empty] | verify data |  |  |  | 74500
6000 | 1ST CHOICE |  |  |  | 1ST CHOICE |  |  |  |  | 91000

## Circuit Breakers
Circuit Breakers
Current | Current | CB Rating | Formula Test
(A) | (A) | (A) | Enter Current | 1204.7 | (A)
0 | 0 | Check | CB Rating: | 1200 | (A)
1 | 1.004 | 5
5 | 5.02 | 10
10 | 10.04 | 15
15 | 15.06 | 20
20 | 20.08 | 25
25 | 25.1 | 30
30 | 30.12 | 40
40 | 40.16 | 50
50 | 50.2 | 60
60 | 60.24 | 60
63 | 63.252 | 70
70 | 70.28 | 80
80 | 80.32 | 90
90 | 90.36 | 100
100 | 100.4 | 110
110 | 110.44 | 125
125 | 125.5 | 150
150 | 150.6 | 175
175 | 175.7 | 200
200 | 200.8 | 225
225 | 225.9 | 250
250 | 251 | 300
300 | 301.2 | 350
350 | 351.4 | 400
400 | 401.6 | 450
450 | 451.8 | 500
500 | 502 | 600
600 | 602.4 | 700
700 | 702.8 | 800
800 | 803.2 | 900
900 | 903.6 | 1000
1000 | 1004 | 1200
1200 | 1204.8 | Check

## Air Conditionning
Manufact | Model | BTU | Kw | NEMA | size HxWxD | Mounting | H | W | D | ARM450 | ARM600 | ARM800 | ARM1250 | Vdc | Adc | ARM | W | H | D | BTU reqd | BTU dissip
Kooltronic | 1RP17 | 1000 | 0.29307 | 12 | 17.5x12.5x11 | SIDE | 17.5 | 12.5 | 11 | 450 | 600 | 800 | 1250 | 400 | 5 | 450 | 24 | 30 | 16 | 336.9891 | 699.4891
Hammond | DTS1200 | 1200 | 0.35169 | 12 | 13x14.76x7.5 | SIDE | 13 | 14.76 | 7.5 | 450 | 600 | 800 | 1250 | 400 | 9 | 450 | 24 | 30 | 16 | 824.9254 | 1187.4254
Vortec | 516X | 1600 | 0.46891 | 4X | 23x10x8.75 | SIDE | 23 | 10 | 8.75 | 450 | 600 | 800 | 1250 | 400 | 18 | 600 | 24 | 48 | 16 | 1824.8508 | 2374.8508
Vortec | 518 | 1800 | 0.52753 | 12 | 17.75x12x8.75 | SIDE | 17.75 | 12 | 8.75 | 450 | 600 | 800 | 1250 | 400 | 27 | 600 | 24 | 48 | 16 | 3012.2762 | 3562.2762
Kooltronic | 2RP17 | 2000 | 0.58614 | 12 | 17.5x12.5x11 | SIDE | 17.5 | 12.5 | 11 | 450 | 600 | 800 | 1250 | 400 | 36 | 600 | 24 | 48 | 16 | 4199.7017 | 4749.7017
Kooltronic | 2RP28 | 2000 | 0.58614 | 12 | 28x12.5x11 | SIDE | 28 | 12.5 | 11 | 450 | 600 | 800 | 1250 | 400 | 41 | 600 | 24 | 48 | 16 | 4848.0086 | 5398.0086
Hammond | DTS2000 | 2000 | 0.58614 | 12 | 17.5x12.5x10 | SIDE | 17.5 | 12.5 | 10 | 450 | 600 | 800 | 1250 | 400 | 45 | 600 | 24 | 48 | 16 | 5489.4913 | 6039.4913
Hammond | DTS2000SS | 2000 | 0.58614 | 4X | 19.5x15.1x15.1 | SIDE | 19.5 | 15.1 | 15.1 | 450 | 600 | 800 | 1250 | 400 | 54 | 600 | 24 | 48 | 16 | 6574.5525 | 7124.5525
Vortec | 522X | 2200 | 0.64476 | 4X | 29.5x15.75x8.75 | SIDE | 29.5 | 15.75 | 8.75 | 450 | 600 | 800 | 1250 | 400 | 63 | 800 | 34 | 48 | 28 | 7515.3838 | 8414.3422
Kooltronic | 3P21R | 3000 | 0.87921 | 4X | 21.25x12x12.5 | SIDE | 21.25 | 12 | 12.5 | 450 | 600 | 800 | 1250 | 400 | 72 | 800 | 34 | 48 | 28 | 8600.445 | 9499.4033
Kooltronic | 4RP28 | 4000 | 1.1723 | 12 | 28x12.5x11 | SIDE | 28 | 12.5 | 11 | 450 | 600 | 800 | 1250 | 400 | 81 | 800 | 34 | 48 | 28 | 9685.5062 | 10584.4645
Vortec | 540 | 4000 | 1.1723 | 12 | 28.5x17x11.5 | SIDE | 28.5 | 17 | 11.5 | 450 | 600 | 800 | 1250 | 400 | 108 | 800 | 34 | 48 | 28 | 13350.1467 | 14249.105
Vortec | 540X | 4000 | 1.1723 | 4X | 29.5x15.75x8.75 | SIDE | 29.5 | 15.75 | 8.75 | 450 | 600 | 800 | 1250 | 400 | 135 | 800 | 34 | 48 | 28 | 16810.0586 | 17709.017
Hammond | DTS4500 | 4500 | 1.3188 | 12 | 16x23.75x15.5 | TOP | 16 | 23.75 | 15.5 | 450 | 600 | 800 | 1250 | 400 | 144 | 800 | 34 | 48 | 28 | 18099.8483 | 18998.8067
Kooltronic | 1P32 | 1000 | 0.29307 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | 600 | 800 | 1250 | 400 | 180 | 1250 | 38 | 70 | 28 | 22202.1131 | 23543.7798
Kooltronic | 2RP33 | 2000 | 0.58614 | 12 | 32.75x12.5x11 | SIDE | 32.75 | 12.5 | 11 | N/A | 600 | 800 | 1250 | 400 | 216 | 1250 | 38 | 70 | 28 | 26951.8148 | 28293.4815
Kooltronic | 2P32 | 2000 | 0.58614 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | 600 | 800 | 1250
Vortec | 518T | 2200 | 0.64476 | 12 | 10.25x17x21 | TOP | 10.25 | 17 | 21 | N/A | N/A | 800 | 1250
Kooltronic | 3P32 | 3000 | 0.87921 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | 600 | 800 | 1250
Hammond | DTS3500 | 3500 | 1.0257 | 12 | 36x15.5x8 | SIDE | 36 | 15.5 | 8 | N/A | 600 | 800 | 1250 | Vdc | Adc | ARM | W | H | D | BTU reqd
Kooltronic | 4RP33 | 4000 | 1.1723 | 12 | 32.75x12.5x11 | SIDE | 32.75 | 12.5 | 11 | N/A | 600 | 800 | 1250 | 600 | 5 | 450 | 24 | 30 | 16 | 592.8998 | 955.3998
Kooltronic | 4RP36 | 4000 | 1.1723 | 12 | 36.75X15.5X11 | SIDE | 36.75 | 15.5 | 11 | N/A | 600 | 800 | 1250 | 600 | 9 | 450 | 24 | 30 | 16 | 1336.7467 | 1699.2467
Kooltronic | 4RP47 | 4000 | 1.1723 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | 600 | 800 | 1250 | 600 | 18 | 600 | 24 | 48 | 16 | 2848.4934 | 3398.4934
Kooltronic | 4P32 | 4000 | 1.1723 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | 600 | 800 | 1250 | 600 | 27 | 600 | 24 | 48 | 16 | 4547.7401 | 5097.7401
Kooltronic | 4P38 | 4000 | 1.1723 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 36 | 600 | 24 | 48 | 16 | 6246.9869 | 6796.9869
Kooltronic | 4P47 | 4000 | 1.1723 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 41 | 600 | 24 | 48 | 16 | 7304.7509 | 7854.7509
Kooltronic | 5P38 | 5000 | 1.4654 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 45 | 600 | 24 | 48 | 16 | 7946.2336 | 8496.2336
Kooltronic | 5P47 | 5000 | 1.4654 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 54 | 800 | 34 | 48 | 28 | 9296.522 | 10195.4803
Kooltronic | 6RP36 | 6000 | 1.7584 | 12 | 36.75X15.5X11 | SIDE | 36.75 | 15.5 | 11 | N/A | 600 | 800 | 1250 | 600 | 63 | 800 | 34 | 48 | 28 | 10995.7687 | 11894.727
Kooltronic | 6RP47 | 6000 | 1.7584 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | 600 | 800 | 1250 | 600 | 72 | 800 | 34 | 48 | 28 | 12695.0154 | 13593.9737
Kooltronic | 6P38 | 6000 | 1.7584 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 81 | 800 | 34 | 48 | 28 | 14394.2621 | 15293.2204
Kooltronic | 6P47 | 6000 | 1.7584 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 108 | 800 | 34 | 48 | 28 | 19492.0023 | 20390.9606
Vortec | 560 | 6000 | 1.7584 | 12 | 38.75x15x11.5 | SIDE | 38.75 | 15 | 11.5 | N/A | 600 | 800 | 1250 | 600 | 135 | 800 | 34 | 48 | 28 | 24589.7424 | 25488.7007
Hammond | DTS6000 | 6000 | 1.7584 | 12 | 53.15x15.5x8 | SIDE | 53.15 | 15.5 | 8 | N/A | N/A | NA | 1250 | 600 | 144 | 800 | 34 | 48 | 28 | 26288.9891 | 27187.9475
Kooltronic | 7P38 | 7000 | 2.0515 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 180 | 1250 | 38 | 70 | 28 | 32643.2677 | 33984.9343
Kooltronic | 7P47 | 7000 | 2.0515 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250 | 600 | 216 | 1250 | 38 | 70 | 28 | 39235.526 | 40577.1927
Hammond | DTS8000 | 8000 | 2.3446 | 12 | 53.15x15.75x10.75 | SIDE | 53.15 | 15.75 | 10.75 | N/A | N/A | NA | 1250
Kooltronic | 8RP47 | 8000 | 2.3446 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | 600 | 800 | 1250
Kooltronic | 8P38 | 8000 | 2.3446 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250
Kooltronic | 8P47 | 8000 | 2.3446 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250
Vortec | 585X | 8500 | 2.4911 | 4X | 43.5x15.75x10.25 | SIDE | 43.5 | 15.75 | 10.25 | N/A | 600 | 800 | 1250
Kooltronic | 9P38 | 9000 | 2.6376 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250
Kooltronic | 9P47 | 9000 | 2.6376 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250
Kooltronic | 10RP47 | 10000 | 2.9307 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | 600 | 800 | 1250
Kooltronic | 10P38 | 10000 | 2.9307 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | 800 | 1250
Kooltronic | 12RP47 | 12000 | 3.5169 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | 600 | 800 | 1250
Kooltronic | 10P47 | 10000 | 2.9307 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | 800 | 1250
Hammond | DTS12000 | 12000 | 3.5169 | 12 | 53.15x15.75x10.75 | SIDE | 53.15 | 15.75 | 10.75 | N/A | N/A | NA | 1250
Kooltronic | 14RP52 | 14000 | 4.103 | 12 | 52.5x17.25x15.75 | SIDE | 52.5 | 17.25 | 15.75 | N/A | N/A | NA | 1250
Kooltronic | 16RP52 | 16000 | 4.6891 | 12 | 52.5x17.25x15.75 | SIDE | 52.5 | 17.25 | 15.75 | N/A | N/A | NA | 1250
Kooltronic | 18RP52 | 18000 | 5.2753 | 12 | 52.5x17.25x15.75 | SIDE | 52.5 | 17.25 | 15.75 | N/A | N/A | NA | 1250
Kooltronic | 20RP55 | 20000 | 5.8614 | 12 | 55x22x17 | SIDE | 55 | 22 | 17 | N/A | N/A | NA | 1250
Kooltronic | 22RP55 | 22000 | 6.4476 | 12 | 55x22x17 | SIDE | 55 | 22 | 17 | N/A | N/A | NA | 1250

## Cooling Data
Specs: | [7 empty] | VORTEX
Output |  | NEMA 12 | NEMA 4 |  | NEMA 4X |  |  |  |  | NEMA 3R | NEMA 12 | NEMA 4 | NEMA 4X
Vdc | Idc | IP54 | IP65 |  | IP65 |  |  | btu | SCFM | $ | $ | $ | $
(V) | (A) | Fan | AC | Vortex | AC | Vortex |  | 400 | 8 |  | 349
[8 empty] | 900 | 15 |  | 476 | 539 | 875
600 | 5 | [6 empty] | 1500/1700 | 25 |  | 476 | 539 | 875
600 | 9 | [6 empty] | 2500 | 35 |  | 541 | 612 | 915
600 | 18 | [6 empty] | 5000 | 70 |  | 859 | 879 | 1214
600 | 27
600 | 36 | [6 empty] | AC
600 | 41 | [8 empty] | NEMA 3R | NEMA 12 | NEMA 4 | NEMA 4X
600 | 45 | [6 empty] | btu |  | $ | $ | $ | $
600 | 54 | [6 empty] | 1000 |  |  | 2910 | -
600 | 63 | [6 empty] | 2000 |  |  | 3200 | - | 7720
600 | 72 | [6 empty] | 3000 |  |  |  | -
600 | 81 | [6 empty] | 3500 |  |  | 3800
600 | 108 | [6 empty] | 4000 |  |  |  | -
600 | 135 | [6 empty] | 5000 |  |  |  | -
600 | 144 | [6 empty] | 6000 |  |  | 4600 | -
600 | 180 | [6 empty] | 7000 |  |  |  | -
600 | 216 | [6 empty] | 8000 |  |  | 5300 | -
[8 empty] | 9000 |  |  |  | -
[8 empty] | 10000 |  |  |  | -
[8 empty] | 11000 |  |  |  | -
Specs: | [7 empty] | 12000 |  |  | 6900 | -
Output |  | NEMA 12 | NEMA 4 |  | NEMA 4X |  |  | 13000 |  |  |  | -
Vdc | Idc | IP54 | IP65 |  | IP65 |  |  | 14000 |  |  |  | -
(V) | (A) | Fan | AC | Vortex | AC | Vortex |  | 15000 |  |  |  | -
FAN
400 | 5 | [8 empty] | NEMA 3R | NEMA 12 | NEMA 4 | NEMA 4X
400 | 9 | [6 empty] | CFM |  | $ | $ | $ | $
400 | 18
400 | 27
400 | 36
400 | 41
400 | 45
400 | 54 | [6 empty] | Filter
400 | 63 | [6 empty] | PFA 3000 | 50
400 | 72 | [6 empty] | PFA 5000 | 60
400 | 81
400 | 108
400 | 135
400 | 144
400 | 180
400 | 216
[5 empty] | H x W x D |  | H | W | D | ARM450 | ARM600 | ARM800 | ARM1250
Manufact | Model | BTU | Kw | NEMA | size | Mounting
Kooltronic | 1RP17 | 1000 | 0.29307 | 12 | 17.5x12.5x11 | SIDE | 17.5 | 12.5 | 11 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 1P32 | 1000 | 0.29307 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | ARM600 | ARM800 | ARM1250
Hammond | DTS1200 | 1200 | 0.35169 | 12 | 13x14.76x7.5 | SIDE | 13 | 14.76 | 7.5 | ARM450 | ARM600 | ARM800 | ARM1250
Vortec | 516X | 1600 | 0.46891 | 4X | 23x10x8.75 | SIDE | 23 | 10 | 8.75 | ARM450 | ARM600 | ARM800 | ARM1250
Vortec | 518 | 1800 | 0.52753 | 12 | 17.75x12x8.75 | SIDE | 17.75 | 12 | 8.75 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 2RP17 | 2000 | 0.58614 | 12 | 17.5x12.5x11 | SIDE | 17.5 | 12.5 | 11 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 2RP28 | 2000 | 0.58614 | 12 | 28x12.5x11 | SIDE | 28 | 12.5 | 11 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 2RP33 | 2000 | 0.58614 | 12 | 32.75x12.5x11 | SIDE | 32.75 | 12.5 | 11 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 2P32 | 2000 | 0.58614 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | ARM600 | ARM800 | ARM1250
Hammond | DTS2000 | 2000 | 0.58614 | 12 | 17.5x12.5x10 | SIDE | 17.5 | 12.5 | 10 | ARM450 | ARM600 | ARM800 | ARM1250
Hammond | DTS2000SS | 2000 | 0.58614 | 4X | 19.5x15.1x15.1 | SIDE | 19.5 | 15.1 | 15.1 | ARM450 | ARM600 | ARM800 | ARM1250
Vortec | 518T | 2200 | 0.64476 | 12 | 10.25x17x21 | TOP | 10.25 | 17 | 21 | N/A | N/A | ARM800 | ARM1250
Vortec | 522X | 2200 | 0.64476 | 4X | 29.5x15.75x8.75 | SIDE | 29.5 | 15.75 | 8.75 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 3P21R | 3000 | 0.87921 | 4X | 21.25x12x12.5 | SIDE | 21.25 | 12 | 12.5 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 3P32 | 3000 | 0.87921 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | ARM600 | ARM800 | ARM1250
Hammond | DTS3500 | 3500 | 1.0257 | 12 | 36x15.5x8 | SIDE | 36 | 15.5 | 8 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 4RP28 | 4000 | 1.1723 | 12 | 28x12.5x11 | SIDE | 28 | 12.5 | 11 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 4RP33 | 4000 | 1.1723 | 12 | 32.75x12.5x11 | SIDE | 32.75 | 12.5 | 11 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 4RP36 | 4000 | 1.1723 | 12 | 36.75X15.5X11 | SIDE | 36.75 | 15.5 | 11 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 4RP47 | 4000 | 1.1723 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 4P32 | 4000 | 1.1723 | 4X | 32.25x14.5x13 | SIDE | 32.25 | 14.5 | 13 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 4P38 | 4000 | 1.1723 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 4P47 | 4000 | 1.1723 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Vortec | 540 | 4000 | 1.1723 | 12 | 28.5x17x11.5 | SIDE | 28.5 | 17 | 11.5 | ARM450 | ARM600 | ARM800 | ARM1250
Vortec | 540X | 4000 | 1.1723 | 4X | 29.5x15.75x8.75 | SIDE | 29.5 | 15.75 | 8.75 | ARM450 | ARM600 | ARM800 | ARM1250
Hammond | DTS4500 | 4500 | 1.3188 | 12 | 16x23.75x15.5 | TOP | 16 | 23.75 | 15.5 | ARM450 | ARM600 | ARM800 | ARM1250
Kooltronic | 5P38 | 5000 | 1.4654 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 5P47 | 5000 | 1.4654 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 6RP36 | 6000 | 1.7584 | 12 | 36.75X15.5X11 | SIDE | 36.75 | 15.5 | 11 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 6RP47 | 6000 | 1.7584 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 6P38 | 6000 | 1.7584 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 6P47 | 6000 | 1.7584 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Vortec | 560 | 6000 | 1.7584 | 12 | 38.75x15x11.5 | SIDE | 38.75 | 15 | 11.5 | N/A | ARM600 | ARM800 | ARM1250
Hammond | DTS6000 | 6000 | 1.7584 | 12 | 53.15x15.5x8 | SIDE | 53.15 | 15.5 | 8 | N/A | N/A | NA | ARM1250
Kooltronic | 7P38 | 7000 | 2.0515 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 7P47 | 7000 | 2.0515 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Hammond | DTS8000 | 8000 | 2.3446 | 12 | 53.15x15.75x10.75 | SIDE | 53.15 | 15.75 | 10.75 | N/A | N/A | NA | ARM1250
Kooltronic | 8RP47 | 8000 | 2.3446 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 8P38 | 8000 | 2.3446 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 8P47 | 8000 | 2.3446 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Vortec | 585X | 8500 | 2.4911 | 4X | 43.5x15.75x10.25 | SIDE | 43.5 | 15.75 | 10.25 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 9P38 | 9000 | 2.6376 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 9P47 | 9000 | 2.6376 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 10RP47 | 10000 | 2.9307 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 10P38 | 10000 | 2.9307 | 4X | 37.75x18.75x18 | SIDE | 37.75 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Kooltronic | 12RP47 | 12000 | 3.5169 | 12 | 47.25X15.5X13.5 | SIDE | 47.25 | 15.5 | 13.5 | N/A | ARM600 | ARM800 | ARM1250
Kooltronic | 10P47 | 10000 | 2.9307 | 4X | 47x18.75x18 | SIDE | 47 | 18.75 | 18 | N/A | N/A | ARM800 | ARM1250
Hammond | DTS12000 | 12000 | 3.5169 | 12 | 53.15x15.75x10.75 | SIDE | 53.15 | 15.75 | 10.75 | N/A | N/A | NA | ARM1250
Kooltronic | 14RP52 | 14000 | 4.103 | 12 | 52.5x17.25x15.75 | SIDE | 52.5 | 17.25 | 15.75 | N/A | N/A | NA | ARM1250
Kooltronic | 16RP52 | 16000 | 4.6891 | 12 | 52.5x17.25x15.75 | SIDE | 52.5 | 17.25 | 15.75 | N/A | N/A | NA | ARM1250
Kooltronic | 18RP52 | 18000 | 5.2753 | 12 | 52.5x17.25x15.75 | SIDE | 52.5 | 17.25 | 15.75 | N/A | N/A | NA | ARM1250
Kooltronic | 20RP55 | 20000 | 5.8614 | 12 | 55x22x17 | SIDE | 55 | 22 | 17 | N/A | N/A | NA | ARM1250
Kooltronic | 22RP55 | 22000 | 6.4476 | 12 | 55x22x17 | SIDE | 55 | 22 | 17 | N/A | N/A | NA | ARM1250

## AC Line Reactor+Harmonic Filter
3 PHASE Battery Chargers | [5 empty] | VERIFIER LES COEFFICIENT DES TRANSFOS AVEC DES MODELES EXISTANTS
Harmoniques
%
Vnom | Idc | #cel | VPC | Vmax | Vsec | Isec | Psec |  | P | Iprim | At Vac | [9 empty] | 1 | 100
(Vdc) | (Idc) |  | (Vdc) | (Vdc) | (Vac) | (Iac) | (Kva) |  | (Kva) | (Iac) | (Vac) | [9 empty] | 2 | 0
[21 empty] | 3 | 0
Vnom: Specs:; Psec: Transformer Sizing (3 Phase) |  |  |  |  | Impedance |  |  | Line Reactor |  | Harmonic Capacitor |  |  |  | 4 | 0
Vnom: Vnom; #cel: Output; Vmax: Input | [13 empty] | 5 | 30
380 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch |  |  | 6 | 0
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr |  |  | 7 | 12
[21 empty] | 8 | 0
190 | 1.65 | 313.5 | 5 | 120 | 12.0281 | 10 | 147.5958 | 255.6434 | 25 | 5.1875 | 2.5 | [9 empty] | 9 | 0
120 | 6 | 720 | 40 | 480 | 51.721 | 10 | 338.976 | 587.1237 | 25 | 41.5 | 43 | [9 empty] | 10 | 0
[21 empty] | 11 | 9
255.6434
Specs: | [6 empty] | Transformer Sizing (3 phase)
Vnom: Vnom; #cel: Output; Vmax: Input |  |  |  |  | TX Impedance |  |  | at 5% | at 4%
12 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | Ll | Ll | I5 | Ch | Config = Y | Config = Δ
#cel | (V) | (V) | (A) | (V) | (A) | 25 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr | (μF) | (μF)
24 | 2.4 | 57.6 | 175 | 480 | 21.6506 | 25 | 32.816 | 56.839 | 25 | 181.5625 | 18
60 | 2.4 | 144 | 100 | 480 | 28.8675 | 25 | 77.04 | 133.4372 | 25 | 103.75 | 24
60 | 2.4 | 144 | 150 | 480 | 43.3013 | 25 | 77.04 | 133.4372 | 25 | 155.625 | 36
6 | 2.4 | 14.4 | 20 | 120 | 3.6084 | 25 | 9.704 | 16.8078 | 25 | 20.75 | 0.75
6 | 2.4 | 14.4 | 25 | 120 | 4.8113 | 25 | 9.704 | 16.8078 | 25 | 25.9375 | 1
6 | 2.4 | 14.4 | 30 | 120 | 4.8113 | 25 | 9.704 | 16.8078 | 25 | 31.125 | 1
6 | 2.4 | 14.4 | 35 | 120 | 6.0141 | 25 | 9.704 | 16.8078 | 25 | 36.3125 | 1.25
6 | 2.4 | 14.4 | 40 | 120 | 6.0141 | 25 | 9.704 | 16.8078 | 25 | 41.5 | 1.25
6 | 2.4 | 14.4 | 50 | 120 | 8.4197 | 25 | 9.704 | 16.8078 | 25 | 51.875 | 1.75
6 | 2.4 | 14.4 | 60 | 120 | 9.6225 | 25 | 9.704 | 16.8078 | 25 | 62.25 | 2
6 | 2.4 | 14.4 | 75 | 120 | 12.0281 | 25 | 9.704 | 16.8078 | 25 | 77.8125 | 2.5
6 | 2.4 | 14.4 | 100 | 120 | 15.6366 | 25 | 9.704 | 16.8078 | 25 | 103.75 | 3.25
6 | 2.4 | 14.4 | 125 | 120 | 19.245 | 25 | 9.704 | 16.8078 | 25 | 129.6875 | 4
6 | 2.4 | 14.4 | 150 | 120 | 22.8534 | 25 | 9.704 | 16.8078 | 25 | 155.625 | 4.75
6 | 2.4 | 14.4 | 175 | 120 | 26.4619 | 25 | 9.704 | 16.8078 | 25 | 181.5625 | 5.5
6 | 2.4 | 14.4 | 200 | 120 | 30.0703 | 25 | 9.704 | 16.8078 | 25 | 207.5 | 6.25
6 | 2.4 | 14.4 | 250 | 120 | 37.2872 | 25 | 9.704 | 16.8078 | 25 | 259.375 | 7.75
6 | 2.4 | 14.4 | 300 | 208 | 25.6754 | 25 | 9.704 | 16.8078 | 25 | 311.25 | 9.25
6 | 2.4 | 14.4 | 350 | 208 | 30.5329 | 25 | 9.704 | 16.8078 | 25 | 363.125 | 11
6 | 2.4 | 14.4 | 400 | 208 | 34.6965 | 25 | 9.704 | 16.8078 | 25 | 415 | 12.5
6 | 2.4 | 14.4 | 450 | 208 | 38.8601 | 25 | 9.704 | 16.8078 | 25 | 466.875 | 14
6 | 2.4 | 14.4 | 500 | 208 | 43.0237 | 25 | 9.704 | 16.8078 | 25 | 518.75 | 15.5
6 | 2.4 | 14.4 | 600 | 480 | 22.252 | 25 | 9.704 | 16.8078 | 25 | 622.5 | 18.5
6 | 2.4 | 14.4 | 700 | 480 | 26.4619 | 25 | 9.704 | 16.8078 | 25 | 726.25 | 22
6 | 2.4 | 14.4 | 800 | 480 | 30.0703 | 25 | 9.704 | 16.8078 | 25 | 830 | 25
6 | 2.4 | 14.4 | 900 | 480 | 33.6788 | 25 | 9.704 | 16.8078 | 25 | 933.75 | 28
6 | 2.4 | 14.4 | 1000 | 480 | 37.2872 | 25 | 9.704 | 16.8078 | 25 | 1037.5 | 31
6 | 2.4 | 14.4 | 1100 | 480 | 40.8956 | 25 | 9.704 | 16.8078 | 25 | 1141.25 | 34
6 | 2.4 | 14.4 | 1200 | 480 | 44.5041 | 25 | 9.704 | 16.8078 | 25 | 1245 | 37
Specs: | [6 empty] | Transformer Sizing (3 phase)
Vnom |  | Output |  | Input
24 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr
12 | 2.4 | 28.8 | 5 | 120 | 1.2028 | 10 | 15.559 | 26.949 | 25 | 5.1875 | 0.25
12 | 2.4 | 28.8 | 10 | 120 | 2.4056 | 10 | 15.559 | 26.949 | 25 | 10.375 | 0.5
12 | 2.4 | 28.8 | 15 | 120 | 3.6084 | 10 | 15.559 | 26.949 | 25 | 15.5625 | 0.75
12 | 2.4 | 28.8 | 20 | 120 | 4.8113 | 10 | 15.559 | 26.949 | 25 | 20.75 | 1
12 | 2.4 | 28.8 | 25 | 120 | 6.0141 | 10 | 15.559 | 26.949 | 25 | 25.9375 | 1.25
12 | 2.4 | 28.8 | 30 | 120 | 7.2169 | 10 | 15.559 | 26.949 | 25 | 31.125 | 1.5
12 | 2.4 | 28.8 | 35 | 120 | 8.4197 | 10 | 15.559 | 26.949 | 25 | 36.3125 | 1.75
12 | 2.4 | 28.8 | 40 | 120 | 9.6225 | 10 | 15.559 | 26.949 | 25 | 41.5 | 2
12 | 2.4 | 28.8 | 50 | 120 | 12.0281 | 10 | 15.559 | 26.949 | 25 | 51.875 | 2.5
12 | 2.4 | 28.8 | 60 | 120 | 14.4338 | 10 | 15.559 | 26.949 | 25 | 62.25 | 3
12 | 2.4 | 28.8 | 75 | 120 | 18.0422 | 10 | 15.559 | 26.949 | 25 | 77.8125 | 3.75
12 | 2.4 | 28.8 | 100 | 120 | 24.0563 | 10 | 15.559 | 26.949 | 25 | 103.75 | 5
12 | 2.4 | 28.8 | 125 | 120 | 30.0703 | 10 | 15.559 | 26.949 | 25 | 129.6875 | 6.25
12 | 2.4 | 28.8 | 150 | 120 | 36.0844 | 10 | 15.559 | 26.949 | 25 | 155.625 | 7.5
12 | 2.4 | 28.8 | 175 | 120 | 40.8956 | 10 | 15.559 | 26.949 | 25 | 181.5625 | 8.5
12 | 2.4 | 28.8 | 200 | 208 | 27.0633 | 10 | 15.559 | 26.949 | 25 | 207.5 | 9.75
12 | 2.4 | 28.8 | 250 | 208 | 34.6965 | 10 | 15.559 | 26.949 | 25 | 259.375 | 12.5
12 | 2.4 | 28.8 | 300 | 208 | 41.6358 | 10 | 15.559 | 26.949 | 25 | 311.25 | 15
12 | 2.4 | 28.8 | 350 | 240 | 40.8956 | 10 | 15.559 | 26.949 | 25 | 363.125 | 17
12 | 2.4 | 28.8 | 400 | 480 | 23.4549 | 10 | 15.559 | 26.949 | 25 | 415 | 19.5
12 | 2.4 | 28.8 | 450 | 480 | 26.4619 | 10 | 15.559 | 26.949 | 25 | 466.875 | 22
12 | 2.4 | 28.8 | 500 | 480 | 30.0703 | 10 | 15.559 | 26.949 | 25 | 518.75 | 25
12 | 2.4 | 28.8 | 600 | 480 | 36.0844 | 10 | 15.559 | 26.949 | 25 | 622.5 | 30
12 | 2.4 | 28.8 | 700 | 480 | 40.8956 | 10 | 15.559 | 26.949 | 25 | 726.25 | 34
12 | 2.4 | 28.8 | 800 | 480 | 46.9097 | 10 | 15.559 | 26.949 | 25 | 830 | 39
12 | 2.4 | 28.8 | 900 | 480 | 52.9238 | 10 | 15.559 | 26.949 | 25 | 933.75 | 44
12 | 2.4 | 28.8 | 1000 | 480 | 58.9378 | 10 | 15.559 | 26.949 | 25 | 1037.5 | 49
12 | 2.4 | 28.8 | 1100 | 480 | 64.9519 | 10 | 15.559 | 26.949 | 25 | 1141.25 | 54
12 | 2.4 | 28.8 | 1200 | 480 | 70.966 | 10 | 15.559 | 26.949 | 25 | 1245 | 59
Specs: | [6 empty] | Transformer Sizing (3 phase)
Vnom |  | Output |  | Input
36 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr
18 | 2.4 | 43.2 | 5 | 120 | 2.4056 | 10 | 22.3386 | 38.6915 | 25 | 5.1875 | 0.5
18 | 2.4 | 43.2 | 10 | 120 | 3.6084 | 10 | 22.3386 | 38.6915 | 25 | 10.375 | 0.75
18 | 2.4 | 43.2 | 15 | 120 | 6.0141 | 10 | 22.3386 | 38.6915 | 25 | 15.5625 | 1.25
18 | 2.4 | 43.2 | 20 | 120 | 7.2169 | 10 | 22.3386 | 38.6915 | 25 | 20.75 | 1.5
18 | 2.4 | 43.2 | 25 | 120 | 8.4197 | 10 | 22.3386 | 38.6915 | 25 | 25.9375 | 1.75
18 | 2.4 | 43.2 | 30 | 120 | 10.8253 | 10 | 22.3386 | 38.6915 | 25 | 31.125 | 2.25
18 | 2.4 | 43.2 | 35 | 120 | 12.0281 | 10 | 22.3386 | 38.6915 | 25 | 36.3125 | 2.5
18 | 2.4 | 43.2 | 40 | 120 | 14.4338 | 10 | 22.3386 | 38.6915 | 25 | 41.5 | 3
18 | 2.4 | 43.2 | 50 | 120 | 16.8394 | 10 | 22.3386 | 38.6915 | 25 | 51.875 | 3.5
18 | 2.4 | 43.2 | 60 | 120 | 20.4478 | 10 | 22.3386 | 38.6915 | 25 | 62.25 | 4.25
18 | 2.4 | 43.2 | 75 | 120 | 25.2591 | 10 | 22.3386 | 38.6915 | 25 | 77.8125 | 5.25
18 | 2.4 | 43.2 | 100 | 120 | 33.6788 | 10 | 22.3386 | 38.6915 | 25 | 103.75 | 7
18 | 2.4 | 43.2 | 125 | 120 | 42.0985 | 10 | 22.3386 | 38.6915 | 25 | 129.6875 | 8.75
18 | 2.4 | 43.2 | 150 | 208 | 29.1451 | 10 | 22.3386 | 38.6915 | 25 | 155.625 | 10.5
18 | 2.4 | 43.2 | 175 | 208 | 34.6965 | 10 | 22.3386 | 38.6915 | 25 | 181.5625 | 12.5
18 | 2.4 | 43.2 | 200 | 208 | 38.8601 | 10 | 22.3386 | 38.6915 | 25 | 207.5 | 14
18 | 2.4 | 43.2 | 250 | 240 | 42.0985 | 10 | 22.3386 | 38.6915 | 25 | 259.375 | 17.5
18 | 2.4 | 43.2 | 300 | 480 | 25.2591 | 10 | 22.3386 | 38.6915 | 25 | 311.25 | 21
18 | 2.4 | 43.2 | 350 | 480 | 30.0703 | 10 | 22.3386 | 38.6915 | 25 | 363.125 | 25
18 | 2.4 | 43.2 | 400 | 480 | 33.6788 | 10 | 22.3386 | 38.6915 | 25 | 415 | 28
18 | 2.4 | 43.2 | 450 | 480 | 38.49 | 10 | 22.3386 | 38.6915 | 25 | 466.875 | 32
18 | 2.4 | 43.2 | 500 | 480 | 42.0985 | 10 | 22.3386 | 38.6915 | 25 | 518.75 | 35
18 | 2.4 | 43.2 | 600 | 480 | 50.5181 | 10 | 22.3386 | 38.6915 | 25 | 622.5 | 42
18 | 2.4 | 43.2 | 700 | 480 | 58.9378 | 10 | 22.3386 | 38.6915 | 25 | 726.25 | 49
18 | 2.4 | 43.2 | 800 | 480 | 67.3575 | 10 | 22.3386 | 38.6915 | 25 | 830 | 56
18 | 2.4 | 43.2 | 900 | 480 | 75.7772 | 10 | 22.3386 | 38.6915 | 25 | 933.75 | 63
18 | 2.4 | 43.2 | 1000 | 480 | 84.1969 | 10 | 22.3386 | 38.6915 | 25 | 1037.5 | 70
18 | 2.4 | 43.2 | 1100 | 480 | 92.6166 | 10 | 22.3386 | 38.6915 | 25 | 1141.25 | 77
18 | 2.4 | 43.2 | 1200 | 480 | 101.0363 | 10 | 22.3386 | 38.6915 | 25 | 1245 | 84
Vnom: Specs:; Psec: Transformer Sizing (3 phase) |  |  |  |  | Line Reactor Evaluation |  |  |  |  | 5th Harm.
Vnom: Vnom; #cel: Output; Vmax: Input | [7 empty] | Line reactor |  | Current | Capacitor
120 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch | Ch-Y connected | Ch-Δ connected | I7 | Ch | Ch-Y connected | Ch-Δ connected
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | (kVAr) | (μF) | (μF) | (A) | (kVAr) | (μF) | (μF)
60 | 2.4 | 144 | 5 | 120 | 6.0141 | 10 | 67.7952 | 117.4247 | 25 | 5.1875 | 1.25 | 11.52 | 0.6912 | 0.4608 | 1.8335 | 1.2223 | 1.8042 | 0.375 | 69.0777 | 23.0259 |  | 0 | 0
60 | 2.4 | 144 | 10 | 120 | 10.8253 | 10 | 67.7952 | 117.4247 | 25 | 10.375 | 2.25 | 6.4 | 0.384 | 0.256 | 1.0186 | 0.67906 | 3.2476 | 0.675 | 124.3398 | 41.4466 |  | 0 | 0
60 | 2.4 | 144 | 15 | 120 | 15.6366 | 10 | 67.7952 | 117.4247 | 25 | 15.5625 | 3.25 | 4.4308 | 0.26585 | 0.17723 | 0.70518 | 0.47012 | 4.691 | 0.975 | 179.6019 | 59.8673 |  | 0 | 0
60 | 2.4 | 144 | 20 | 120 | 20.4478 | 10 | 67.7952 | 117.4247 | 25 | 20.75 | 4.25 | 3.3882 | 0.20329 | 0.13553 | 0.53925 | 0.3595 | 6.1343 | 1.275 | 234.8641 | 78.288 |  | 0 | 0
60 | 2.4 | 144 | 25 | 120 | 26.4619 | 10 | 67.7952 | 117.4247 | 25 | 25.9375 | 5.5 | 2.6182 | 0.15709 | 0.10473 | 0.4167 | 0.2778 | 7.9386 | 1.65 | 303.9417 | 101.3139 |  | 0 | 0
60 | 2.4 | 144 | 30 | 120 | 31.2731 | 10 | 67.7952 | 117.4247 | 25 | 31.125 | 6.5 | 2.2154 | 0.13292 | 0.088615 | 0.35259 | 0.23506 | 9.3819 | 1.95 | 359.2039 | 119.7346 |  | 0 | 0
60 | 2.4 | 144 | 35 | 120 | 36.0844 | 10 | 67.7952 | 117.4247 | 25 | 36.3125 | 7.5 | 1.92 | 0.1152 | 0.0768 | 0.30558 | 0.20372 | 10.8253 | 2.25 | 414.466 | 138.1553 |  | 0 | 0
60 | 2.4 | 144 | 40 | 120 | 40.8956 | 10 | 67.7952 | 117.4247 | 25 | 41.5 | 8.5 | 1.6941 | 0.10165 | 0.067765 | 0.26963 | 0.17975 | 12.2687 | 2.55 | 469.7281 | 156.576 |  | 0 | 0
24 | 2.4 | 57.6 | 175 | 480 | 19.245 | 10 | 29.1181 | 50.434 | 25 | 181.5625 | 16 | 14.4 | 0.864 | 0.576 | 2.2918 | 1.5279 | 5.7735 | 4.8 | 55.2621 | 18.4207 | 2.3094 | 1.92 | 22.1049 | 7.3683
60 | 2.4 | 144 | 60 | 208 | 36.0844 | 10 | 67.7952 | 117.4247 | 25 | 62.25 | 13 | 3.328 | 0.19968 | 0.13312 | 0.52967 | 0.35311 | 10.8253 | 3.9 | 239.115 | 79.705 |  | 0 | 0
60 | 2.4 | 144 | 75 | 240 | 38.49 | 10 | 67.7952 | 117.4247 | 25 | 77.8125 | 16 | 3.6 | 0.216 | 0.144 | 0.57296 | 0.38197 | 11.547 | 4.8 | 221.0485 | 73.6828 |  | 0 | 0
60 | 2.4 | 144 | 100 | 600 | 21.1695 | 10 | 67.7952 | 117.4247 | 25 | 103.75 | 22 | 16.3636 | 0.98182 | 0.65455 | 2.6044 | 1.7362 | 6.3509 | 6.6 | 48.6307 | 16.2102 |  | 0 | 0
60 | 2.4 | 144 | 125 | 480 | 32.476 | 10 | 67.7952 | 117.4247 | 25 | 129.6875 | 27 | 8.5333 | 0.512 | 0.34133 | 1.3581 | 0.90541 | 9.7428 | 8.1 | 93.2548 | 31.0849 |  | 0 | 0
60 | 2.4 | 144 | 150 | 480 | 38.49 | 10 | 67.7952 | 117.4247 | 25 | 155.625 | 32 | 7.2 | 0.432 | 0.288 | 1.1459 | 0.76394 | 11.547 | 9.6 | 110.5243 | 36.8414 |  | 0 | 0
60 | 2.4 | 144 | 175 | 480 | 44.5041 | 10 | 67.7952 | 117.4247 | 25 | 181.5625 | 37 | 6.227 | 0.37362 | 0.24908 | 0.99106 | 0.66071 | 13.3512 | 11.1 | 127.7937 | 42.5979 |  | 0 | 0
60 | 2.4 | 144 | 200 | 480 | 51.721 | 10 | 67.7952 | 117.4247 | 25 | 207.5 | 43 | 5.3581 | 0.32149 | 0.21433 | 0.85277 | 0.56852 | 15.5163 | 12.9 | 148.517 | 49.5057 |  | 0 | 0
60 | 2.4 | 144 | 250 | 480 | 63.7491 | 10 | 67.7952 | 117.4247 | 25 | 259.375 | 53 | 4.3472 | 0.26083 | 0.17389 | 0.69187 | 0.46125 | 19.1247 | 15.9 | 183.0558 | 61.0186 | 7.6499 | 6.36 | 73.2223 | 24.4074
60 | 2.4 | 144 | 300 | 480 | 76.98 | 10 | 67.7952 | 117.4247 | 25 | 311.25 | 64 | 3.6 | 0.216 | 0.144 | 0.57296 | 0.38197 | 23.094 | 19.2 | 221.0485 | 73.6828 |  | 0 | 0
60 | 2.4 | 144 | 350 | 480 | 89.0082 | 10 | 67.7952 | 117.4247 | 25 | 363.125 | 74 | 3.1135 | 0.18681 | 0.12454 | 0.49553 | 0.33035 | 26.7024 | 22.2 | 255.5874 | 85.1958 | 10.681 | 8.88 | 102.2349 | 34.0783
60 | 2.4 | 144 | 400 | 480 | 102.2391 | 10 | 67.7952 | 117.4247 | 25 | 415 | 85 | 2.7106 | 0.16264 | 0.10842 | 0.4314 | 0.2876 | 30.6717 | 25.5 | 293.5801 | 97.86 |  | 0 | 0
60 | 2.4 | 144 | 450 | 480 | 114.2672 | 10 | 67.7952 | 117.4247 | 25 | 466.875 | 95 | 2.4253 | 0.14552 | 0.097011 | 0.38599 | 0.25733 | 34.2802 | 28.5 | 328.1189 | 109.373 |  | 0 | 0
60 | 2.4 | 144 | 500 | 480 | 127.4982 | 10 | 67.7952 | 117.4247 | 25 | 518.75 | 106 | 2.1736 | 0.13042 | 0.086943 | 0.34594 | 0.23062 | 38.2495 | 31.8 | 366.1116 | 122.0372 | 15.2998 | 12.72 | 146.4447 | 48.8149
60 | 2.4 | 144 | 600 | 480 | 152.7573 | 10 | 67.7952 | 117.4247 | 25 | 622.5 | 127 | 1.8142 | 0.10885 | 0.072567 | 0.28873 | 0.19249 | 45.8272 | 38.1 | 438.6432 | 146.2144 |  | 0 | 0
60 | 2.4 | 144 | 700 | 480 | 178.0163 | 10 | 67.7952 | 117.4247 | 25 | 726.25 | 148 | 1.5568 | 0.093405 | 0.06227 | 0.24777 | 0.16518 | 53.4049 | 44.4 | 511.1747 | 170.3916 |  | 0 | 0
60 | 2.4 | 144 | 800 | 480 | 203.2754 | 10 | 67.7952 | 117.4247 | 25 | 830 | 169 | 1.3633 | 0.081799 | 0.054533 | 0.21698 | 0.14465 | 60.9826 | 50.7 | 583.7063 | 194.5688 |  | 0 | 0
60 | 2.4 | 144 | 900 | 480 | 228.5345 | 10 | 67.7952 | 117.4247 | 25 | 933.75 | 190 | 1.2126 | 0.072758 | 0.048505 | 0.193 | 0.12866 | 68.5603 | 57 | 656.2378 | 218.7459 |  | 0 | 0
60 | 2.4 | 144 | 1000 | 480 | 254.9964 | 10 | 67.7952 | 117.4247 | 25 | 1037.5 | 212 | 1.0868 | 0.065208 | 0.043472 | 0.17297 | 0.11531 | 76.4989 | 63.6 | 732.2233 | 244.0744 |  | 0 | 0
60 | 2.4 | 144 | 1100 | 480 | 280.2554 | 10 | 67.7952 | 117.4247 | 25 | 1141.25 | 233 | 0.98884 | 0.05933 | 0.039554 | 0.15738 | 0.10492 | 84.0766 | 69.9 | 804.7548 | 268.2516 |  | 0 | 0
60 | 2.4 | 144 | 1200 | 480 | 305.5145 | 10 | 67.7952 | 117.4247 | 25 | 1245 | 254 | 0.90709 | 0.054425 | 0.036283 | 0.14437 | 0.096245 | 91.6544 | 76.2 | 877.2864 | 292.4288 |  | 0 | 0
[18 empty] | 1.7 | 19.572 | 6.524
Specs: | [6 empty] | Transformer Sizing (3 phase)
Vnom |  | Output |  | Input
72 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr
36 | 2.4 | 86.4 | 5 | 120 | 3.6084 | 10 | 42.6771 | 73.9189 | 25 | 5.1875 | 0.75
36 | 2.4 | 86.4 | 10 | 120 | 7.2169 | 10 | 42.6771 | 73.9189 | 25 | 10.375 | 1.5
36 | 2.4 | 86.4 | 15 | 120 | 9.6225 | 10 | 42.6771 | 73.9189 | 25 | 15.5625 | 2
36 | 2.4 | 86.4 | 20 | 120 | 13.2309 | 10 | 42.6771 | 73.9189 | 25 | 20.75 | 2.75
36 | 2.4 | 86.4 | 25 | 120 | 16.8394 | 10 | 42.6771 | 73.9189 | 25 | 25.9375 | 3.5
36 | 2.4 | 86.4 | 30 | 120 | 19.245 | 10 | 42.6771 | 73.9189 | 25 | 31.125 | 4
36 | 2.4 | 86.4 | 35 | 120 | 22.8534 | 10 | 42.6771 | 73.9189 | 25 | 36.3125 | 4.75
36 | 2.4 | 86.4 | 40 | 120 | 26.4619 | 10 | 42.6771 | 73.9189 | 25 | 41.5 | 5.5
36 | 2.4 | 86.4 | 50 | 120 | 32.476 | 10 | 42.6771 | 73.9189 | 25 | 51.875 | 6.75
36 | 2.4 | 86.4 | 60 | 120 | 38.49 | 10 | 42.6771 | 73.9189 | 25 | 62.25 | 8
36 | 2.4 | 86.4 | 75 | 208 | 27.7572 | 10 | 42.6771 | 73.9189 | 25 | 77.8125 | 10
36 | 2.4 | 86.4 | 100 | 208 | 37.4723 | 10 | 42.6771 | 73.9189 | 25 | 103.75 | 13.5
36 | 2.4 | 86.4 | 125 | 240 | 40.8956 | 10 | 42.6771 | 73.9189 | 25 | 129.6875 | 17
36 | 2.4 | 86.4 | 150 | 480 | 24.0563 | 10 | 42.6771 | 73.9189 | 25 | 155.625 | 20
36 | 2.4 | 86.4 | 175 | 480 | 28.8675 | 10 | 42.6771 | 73.9189 | 25 | 181.5625 | 24
36 | 2.4 | 86.4 | 200 | 480 | 32.476 | 10 | 42.6771 | 73.9189 | 25 | 207.5 | 27
36 | 2.4 | 86.4 | 250 | 480 | 40.8956 | 10 | 42.6771 | 73.9189 | 25 | 259.375 | 34
36 | 2.4 | 86.4 | 300 | 480 | 48.1125 | 10 | 42.6771 | 73.9189 | 25 | 311.25 | 40
36 | 2.4 | 86.4 | 350 | 480 | 56.5322 | 10 | 42.6771 | 73.9189 | 25 | 363.125 | 47
36 | 2.4 | 86.4 | 400 | 480 | 64.9519 | 10 | 42.6771 | 73.9189 | 25 | 415 | 54
36 | 2.4 | 86.4 | 450 | 480 | 72.1688 | 10 | 42.6771 | 73.9189 | 25 | 466.875 | 60
36 | 2.4 | 86.4 | 500 | 480 | 80.5885 | 10 | 42.6771 | 73.9189 | 25 | 518.75 | 67
36 | 2.4 | 86.4 | 600 | 480 | 96.225 | 10 | 42.6771 | 73.9189 | 25 | 622.5 | 80
36 | 2.4 | 86.4 | 700 | 480 | 111.8616 | 10 | 42.6771 | 73.9189 | 25 | 726.25 | 93
36 | 2.4 | 86.4 | 800 | 480 | 128.701 | 10 | 42.6771 | 73.9189 | 25 | 830 | 107
36 | 2.4 | 86.4 | 900 | 480 | 144.3376 | 10 | 42.6771 | 73.9189 | 25 | 933.75 | 120
36 | 2.4 | 86.4 | 1000 | 480 | 159.9741 | 10 | 42.6771 | 73.9189 | 25 | 1037.5 | 133
36 | 2.4 | 86.4 | 1100 | 480 | 176.8135 | 10 | 42.6771 | 73.9189 | 25 | 1141.25 | 147
36 | 2.4 | 86.4 | 1200 | 480 | 192.4501 | 10 | 42.6771 | 73.9189 | 25 | 1245 | 160
Specs: | [6 empty] | Transformer Sizing (3 phase)
Vnom |  | Output |  | Input
120 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr
60 | 2.4 | 144 | 5 | 120 | 6.0141 | 10 | 67.7952 | 117.4247 | 25 | 5.1875 | 1.25
60 | 2.4 | 144 | 10 | 120 | 10.8253 | 10 | 67.7952 | 117.4247 | 25 | 10.375 | 2.25
60 | 2.4 | 144 | 15 | 120 | 15.6366 | 10 | 67.7952 | 117.4247 | 25 | 15.5625 | 3.25
60 | 2.4 | 144 | 20 | 120 | 20.4478 | 10 | 67.7952 | 117.4247 | 25 | 20.75 | 4.25
60 | 2.4 | 144 | 25 | 120 | 26.4619 | 10 | 67.7952 | 117.4247 | 25 | 25.9375 | 5.5
60 | 2.4 | 144 | 30 | 120 | 31.2731 | 10 | 67.7952 | 117.4247 | 25 | 31.125 | 6.5
60 | 2.4 | 144 | 35 | 120 | 36.0844 | 10 | 67.7952 | 117.4247 | 25 | 36.3125 | 7.5
60 | 2.4 | 144 | 40 | 120 | 40.8956 | 10 | 67.7952 | 117.4247 | 25 | 41.5 | 8.5
60 | 2.4 | 144 | 50 | 208 | 30.5329 | 10 | 67.7952 | 117.4247 | 25 | 51.875 | 11
60 | 2.4 | 144 | 60 | 208 | 36.0844 | 10 | 67.7952 | 117.4247 | 25 | 62.25 | 13
60 | 2.4 | 144 | 75 | 240 | 38.49 | 10 | 67.7952 | 117.4247 | 25 | 77.8125 | 16
60 | 2.4 | 144 | 100 | 480 | 26.4619 | 10 | 67.7952 | 117.4247 | 25 | 103.75 | 22
60 | 2.4 | 144 | 125 | 480 | 32.476 | 10 | 67.7952 | 117.4247 | 25 | 129.6875 | 27
60 | 2.4 | 144 | 150 | 480 | 38.49 | 10 | 67.7952 | 117.4247 | 25 | 155.625 | 32
60 | 2.4 | 144 | 175 | 480 | 44.5041 | 10 | 67.7952 | 117.4247 | 25 | 181.5625 | 37
60 | 2.4 | 144 | 200 | 480 | 51.721 | 10 | 67.7952 | 117.4247 | 25 | 207.5 | 43
60 | 2.4 | 144 | 250 | 480 | 63.7491 | 10 | 67.7952 | 117.4247 | 25 | 259.375 | 53
60 | 2.4 | 144 | 300 | 480 | 76.98 | 10 | 67.7952 | 117.4247 | 25 | 311.25 | 64
60 | 2.4 | 144 | 350 | 480 | 89.0082 | 10 | 67.7952 | 117.4247 | 25 | 363.125 | 74
60 | 2.4 | 144 | 400 | 480 | 102.2391 | 10 | 67.7952 | 117.4247 | 25 | 415 | 85
60 | 2.4 | 144 | 450 | 480 | 114.2672 | 10 | 67.7952 | 117.4247 | 25 | 466.875 | 95
60 | 2.4 | 144 | 500 | 480 | 127.4982 | 10 | 67.7952 | 117.4247 | 25 | 518.75 | 106
60 | 2.4 | 144 | 600 | 480 | 152.7573 | 10 | 67.7952 | 117.4247 | 25 | 622.5 | 127
60 | 2.4 | 144 | 700 | 480 | 178.0163 | 10 | 67.7952 | 117.4247 | 25 | 726.25 | 148
60 | 2.4 | 144 | 800 | 480 | 203.2754 | 10 | 67.7952 | 117.4247 | 25 | 830 | 169
60 | 2.4 | 144 | 900 | 480 | 228.5345 | 10 | 67.7952 | 117.4247 | 25 | 933.75 | 190
60 | 2.4 | 144 | 1000 | 480 | 254.9964 | 10 | 67.7952 | 117.4247 | 25 | 1037.5 | 212
60 | 2.4 | 144 | 1100 | 480 | 280.2554 | 10 | 67.7952 | 117.4247 | 25 | 1141.25 | 233
60 | 2.4 | 144 | 1200 | 480 | 305.5145 | 10 | 67.7952 | 117.4247 | 25 | 1245 | 254
Specs: | [6 empty] | Transformer Sizing (3 phase)
Vnom |  | Output |  | Input
240 | Vpc | Vdc max. | Idc | Vin | Iin | Line Fluct % | Vsec l-n | Vsec l-l | Isec safety% | Isec | Psec |  | 5% | 4% | L5 | L4 | I5 | Ch
#cel | (V) | (V) | (A) | (V) | (A) | 10 | (Vac) | (Vac) | 25 | (Iac) | (Kva) | (Ω) | (Ω) | (Ω) | (mH) | (mH) | (A) | kVAr
120 | 2.4 | 288 | 5 | 120 | 10.8253 | 10 | 135.5904 | 234.8495 | 25 | 5.1875 | 2.25
120 | 2.4 | 288 | 10 | 120 | 20.4478 | 10 | 135.5904 | 234.8495 | 25 | 10.375 | 4.25
120 | 2.4 | 288 | 15 | 120 | 31.2731 | 10 | 135.5904 | 234.8495 | 25 | 15.5625 | 6.5
120 | 2.4 | 288 | 20 | 120 | 40.8956 | 10 | 135.5904 | 234.8495 | 25 | 20.75 | 8.5
120 | 2.4 | 288 | 25 | 208 | 30.5329 | 10 | 135.5904 | 234.8495 | 25 | 25.9375 | 11
120 | 2.4 | 288 | 30 | 208 | 36.0844 | 10 | 135.5904 | 234.8495 | 25 | 31.125 | 13
120 | 2.4 | 288 | 35 | 208 | 41.6358 | 10 | 135.5904 | 234.8495 | 25 | 36.3125 | 15
120 | 2.4 | 288 | 40 | 240 | 40.8956 | 10 | 135.5904 | 234.8495 | 25 | 41.5 | 17
120 | 2.4 | 288 | 50 | 480 | 26.4619 | 10 | 135.5904 | 234.8495 | 25 | 51.875 | 22
120 | 2.4 | 288 | 60 | 480 | 31.2731 | 10 | 135.5904 | 234.8495 | 25 | 62.25 | 26
120 | 2.4 | 288 | 75 | 480 | 38.49 | 10 | 135.5904 | 234.8495 | 25 | 77.8125 | 32
120 | 2.4 | 288 | 100 | 480 | 51.721 | 10 | 135.5904 | 234.8495 | 25 | 103.75 | 43
120 | 2.4 | 288 | 125 | 480 | 63.7491 | 10 | 135.5904 | 234.8495 | 25 | 129.6875 | 53
120 | 2.4 | 288 | 150 | 480 | 76.98 | 10 | 135.5904 | 234.8495 | 25 | 155.625 | 64
120 | 2.4 | 288 | 175 | 480 | 89.0082 | 10 | 135.5904 | 234.8495 | 25 | 181.5625 | 74
120 | 2.4 | 288 | 200 | 480 | 102.2391 | 10 | 135.5904 | 234.8495 | 25 | 207.5 | 85
120 | 2.4 | 288 | 250 | 480 | 127.4982 | 10 | 135.5904 | 234.8495 | 25 | 259.375 | 106
120 | 2.4 | 288 | 300 | 480 | 152.7573 | 10 | 135.5904 | 234.8495 | 25 | 311.25 | 127
120 | 2.4 | 288 | 350 | 480 | 178.0163 | 10 | 135.5904 | 234.8495 | 25 | 363.125 | 148
120 | 2.4 | 288 | 400 | 480 | 203.2754 | 10 | 135.5904 | 234.8495 | 25 | 415 | 169
120 | 2.4 | 288 | 450 | 480 | 228.5345 | 10 | 135.5904 | 234.8495 | 25 | 466.875 | 190
120 | 2.4 | 288 | 500 | 480 | 254.9964 | 10 | 135.5904 | 234.8495 | 25 | 518.75 | 212
120 | 2.4 | 288 | 600 | 480 | 305.5145 | 10 | 135.5904 | 234.8495 | 25 | 622.5 | 254
120 | 2.4 | 288 | 700 | 480 | 356.0327 | 10 | 135.5904 | 234.8495 | 25 | 726.25 | 296
120 | 2.4 | 288 | 800 | 480 | 406.5508 | 10 | 135.5904 | 234.8495 | 25 | 830 | 338
120 | 2.4 | 288 | 900 | 480 | 457.069 | 10 | 135.5904 | 234.8495 | 25 | 933.75 | 380
120 | 2.4 | 288 | 1000 | 480 | 508.7899 | 10 | 135.5904 | 234.8495 | 25 | 1037.5 | 423
120 | 2.4 | 288 | 1100 | 480 | 559.3081 | 10 | 135.5904 | 234.8495 | 25 | 1141.25 | 465
120 | 2.4 | 288 | 1200 | 480 | 609.8262 | 10 | 135.5904 | 234.8495 | 25 | 1245 | 507

## Wire-Cables Ampacities
Current | Current | Wire |  | Formula Test
(A) | (A) | AWG |  | Enter Current | 502 | (A) |  | AWG | (A)
0 | 0 | #10 |  | AWG | #4/0 2x |  |  | 24 | 2 | 3.8
4 | 4.016 | #10 | [5 empty] | 22 | 3 | 5.7
6 | 6.024 | #10 | [5 empty] | 20 | 4 | 7.6
9 | 9.036 | #10 | [5 empty] | 18 | 6 | 11.4
15 | 15.06 | #10 | [5 empty] | 16 | 9 | 17.1
22 | 22.088 | #10 | [5 empty] | 14 | 15 | 28.5
40 | 40.16 | #8 | [5 empty] | 12 | 22 | 41.8
60 | 60.24 | #6 | [5 empty] | 10 | 35 | 66.5
80 | 80.32 | #4 | [5 empty] | 8 | 55 | 104.5
105 | 105.42 | #3 | [5 empty] | 6 | 80 | 152
120 | 120.48 | #2 | [5 empty] | 4 | 108 | 205.2
140 | 140.56 | #1 | [5 empty] | 3 | 121 | 229.9
165 | 165.66 | #1/0 | [5 empty] | 2 | 140 | 266
195 | 195.78 | #2/0 |  | 390 | 374.4 | #1/0 |  | 1 | 164 | 311.6
225 | 225.9 | #3/0 |  | 450 | 432 | #2/0 |  | #1/0 | 190 | 361 | 2x #1/0 | 370.5 | 380
260 | 261.04 | #4/0 |  | 520 | 499.2 | #3/0 |  | #2/0 | 221 | 419.9 | 2x #2/0 | 430.95 | 442
300 | 301.2 | 250MCM |  | 600 | 576 | #4/0 |  | #3/0 | 257 | 488.3 | 2x #3/0 | 501.15 | 514
340 | 341.36 | 300MCM | Limite crimper 300 MCM | 680 | 652.8 | 250MCM |  | #4/0 | 300 | 570 | 2x #4/0 | 585 | 600
375 | 376.5 | #2/0 2x |  | 750 | 720 | 300MCM
432 | 433.728 | #3/0 2x
499.2 | 501.1968 | #4/0 2x
576 | 578.304 | 250MCM 2x
652.8 | 655.4112 | 300MCM 2x
720 | 722.88 | Buss
2x #1/0
[5 empty] | 370.5 | 371.982 | 2x #2/0
[5 empty] | 430.95 | 432.6738 | 2x #3/0
[5 empty] | 501.15 | 503.1546 | 2x #4/0
[5 empty] | 585 | 587.34 | BUSS
ALLOWABLE AMPACITIES OF INSULATED COPPER CONDUCTORS INSIDE INDUSTRIAL CONTROL EQUIPMENT ENCLOSURES (BASED ON A ROOM AMBIENT TEMPERATURE OF 40 CELSIUS)
Conductor size,
AWG | Conductors with 90 C insulation | Conductors with 105 C insulation
| In conduit or nonventilated raceway | Open or in ventilated raceway | In conduit or nonventilated raceway | Open or in ventilated raceway
Column 1 | Column 2 | Column 3 | Column 4 | Column 5
24 | 1 | 2 | 1 | 2
22 | 2 | 3 | 2 | 3
20 | 3 | 4 | 3 | 4
18 | 4 | 6 | 4 | 6
16 | 6 | 9 | 6 | 9
14 | 9 | 13 | 10 | 15
12 | 12 | 17 | 15 | 22
10 | 18 | 27 | 22 | 35
8 | 31 | 47 | 35 | 55
6 | 45 | 67 | 52 | 80
4 | 61 | 91 | 71 | 108
3 | 70 | 104 | 80 | 121
2 | 80 | 120 | 90 | 140
1 | 94 | 141 | 107 | 164
1/0 | 110 | 164 | 133 | 190
2/0 | 128 | 191 | 148 | 221
3/0 | 148 | 221 | 171 | 257
4/0 | 173 | 258 | 200 | 300
* Table reference: Burford, Gary. 1995. C22.2 N.14-95 Industrial control equipment table 3: p.70

## Wire-Cable Ampacity Calculation
Internal conductor ampacity | Conductor must be rated 90C or More |  | Relationship between conductor size and overcurrent protection rating for power circuits |  |  |  | Allowable Ampacities of Single-Insulated Conductors Rated 0 Through 2000 Volts in Free Air, Based on Ambient Air Temperature of 30°C (86°F) | [8 empty] | Conductor size | Conductors with 90 C insulation |  | Conductors with 105 C insulation
UL 508A | Table 29.1 |  | UL 508A | Table 66.2 |  |  | NEC | Table 310.17 |  |  | Exemple | Primax
Conductor size |  | Ampacity | Conductor size |  | Maximum rating of nontime-delay fuse or inverse time circuit breaker, amperes | Time delay or dual element fuse, amperes | Conductor size | Conductor Temp Rating 60°C | Conductor Temp Rating 75°C | Conductor Temp Rating 90°C | Conductor Temp Rating 90°C at Ambient = 46-50ºC | Current | Current | Wire |  | AWG | In conduit or nonventilated raceway | Open or in ventilated raceway | In conduit or nonventilated raceway | Open or in ventilated raceway | per UL508A
AWG or kcmil | (mm2) | (A) | AWG or kcmil | (mm2) | (A) | (A) | AWG or kcmil | (A) | (A) | (A) | 0.82 | (A) | (A) | AWG |  | Column 1 | Column 2 | Column 3 | Column 4 | Column 5
18 | -0.82 | 7 | 18 |  |  |  | 18 | — | — | 18 | 14.76 |  |  |  |  | 24 | 1 | 2 | 1 | 2
16 | -1.3 | 10 | 16 |  |  |  | 16 | — | — | 24 | 19.68 |  |  |  |  | 22 | 2 | 3 | 2 | 3
14 | -2.1 | 20 | 14 | 2.1 | 60 | 30 | 14* | 25 | 30 | 35 | 28.7 |  |  |  |  | 20 | 3 | 4 | 3 | 4
12 | -3.3 | 25 | 12 | 3.3 | 80 | 40 | 12* | 30 | 35 | 40 | 32.8 |  |  |  |  | 18 | 4 | 6 | 4 | 6 | 7
10 | -5.3 | 40 | 10 | 5.3 | 100 | 50 | 10* | 40 | 50 | 55 | 45.1 | 40 | 40.16 | #10 |  | 16 | 6 | 9 | 6 | 9 | 10
8 | -8.4 | 60 | 8 | 8.4 | 150 | 80 | 8 | 60 | 70 | 80 | 65.6 | 60 | 60.24 | #8 |  | 14 | 9 | 13 | 10 | 15 | 20
6 | -13.3 | 80 | 6 | 13.3 | 200 | 100 | 6 | 80 | 95 | 105 | 86.1 | 80 | 80.32 | #6 |  | 12 | 12 | 17 | 15 | 22 | 25
4 | -21.2 | 105 | 4 | 21.2 | 250 | 125 | 4 | 105 | 125 | 140 | 114.8 | 105 | 105.42 | #4 |  | 10 | 18 | 27 | 22 | 35 | 40
3 | -26.7 | 120 | 3 | 26.7 | 300 | 150 | 3 | 120 | 145 | 165 | 135.3 | 120 | 120.48 | #3 |  | 8 | 31 | 47 | 35 | 55 | 60
2 | -33.6 | 140 | 2 | 33.6 | 350 | 175 | 2 | 140 | 170 | 190 | 155.8 | 140 | 140.56 | #2 |  | 6 | 45 | 67 | 52 | 80 | 80
1 | -42.4 | 165 | 1 | 42.4 | 400 | 200 | 1 | 165 | 195 | 220 | 180.4 | 165 | 165.66 | #1 |  | 4 | 61 | 91 | 71 | 108 | 105
1/0 | -53.5 | 195 | 1/0 | 53.6 | 500 | 250 | 1/0 | 195 | 230 | 260 | 213.2 | 195 | 195.78 | #1/0 |  | 3 | 70 | 104 | 80 | 121 | 120
2/0 | -67.4 | 225 | 2/0 | 67.4 | 600 | 300 | 2/0 | 225 | 265 | 300 | 246 | 225 | 225.9 | #2/0 |  | 2 | 80 | 120 | 90 | 140 | 140
3/0 | -85 | 260 | 3/0 | 85 | 700 | 350 | 3/0 | 260 | 310 | 350 | 287 | 260 | 261.04 | #3/0 |  | 1 | 94 | 141 | 107 | 164 | 165
4/0 | -107.2 | 300 | 4/0 | 107.2 | 800 | 400 | 4/0 | 300 | 360 | 405 | 332.1 | 300 | 301.2 | #4/0 |  | 1/0 | 110 | 164 | 133 | 190 | 195
250 | -127 | 340 | 250 | – | – | – | 250 | 340 | 405 | 455 | 373.1 | 340 | 341.36 | 250MCM | Crimper Limit | 2/0 | 128 | 191 | 148 | 221 | 225
300 | -152 | 375 | 300 | – | – | – | 300 | 375 | 445 | 505 | 414.1 | 375 | 376.5 | 300MCM |  | 3/0 | 148 | 221 | 171 | 257 | 260
350 | -177 | 420 | 350 | – | – | – | 350 | 420 | 505 | 570 | 467.4 | 432 | 433.728 | #2/0 2x |  | 4/0 | 173 | 258 | 200 | 300 | 300
400 | -203 | 455 | 400 | – | – | – | 400 | 455 | 545 | 615 | 504.3 | 499.2 | 501.1968 | #3/0 2x |  | 250 |  |  |  |  | 340
500 | -253 | 515 | 500 | – | – | – | 500 | 515 | 620 | 700 | 574 | 576 | 578.304 | #4/0 2x |  | 300 |  |  |  |  | 375
600 | -304 | 575 | 600 | – | – | – | 600 | 575 | 690 | 780 | 639.6 | 652.8 | 655.4112 | 250MCM 2x |  | 350 |  |  |  |  | 420
700 | -354 | 630 | 700 | – | – | – | 700 | 630 | 755 | 855 | 701.1 | 720 | 722.88 | 300MCM 2x |  | 400 |  |  |  |  | 455
750 | -380 | 655 | 750 | – | – | – | 750 | 655 | 785 | 885 | 725.7 |  |  | Buss |  | 500 |  |  |  |  | 515
800 | -406 | 680 | 800 | – | – | – | 800 | 680 | 815 | 920 | 754.4 |  |  |  |  | * Table reference: Burford, Gary. 1995. C22.2 N.14-95 Industrial control equipment table 3: p.70
1000 | -508 | 780 | 1000 | – | – | – | 1000 | 780 | 935 | 1055 | 865.1
[7 empty] | CORRECTION FACTORS For ambient temperatures other than 30°C (86°F), multiply the allowable ampacities shown above | For ambient temperatures other than 30°C (86°F), multiply the allowable ampacities by CF
[7 empty] | NEC | Table 310.17
[7 empty] | Ambient Temperature: (deg C) | Conductor Temp Rating 60°C | Conductor Temp Rating 75°C | Conductor Temp Rating 90°C
[7 empty] | 31–35 | 0.91 | 0.94 | 0.96
[7 empty] | 36–40 | 0.82 | 0.88 | 0.91
[7 empty] | 41–45 | 0.71 | 0.82 | 0.87
[7 empty] | 46–50 | 0.58 | 0.75 | 0.82
[7 empty] | 51–55 | 0.41 | 0.67 | 0.76
[7 empty] | 56–60 | — | 0.58 | 0.71
About control panels
Editor:
In reference to "Let's solve your problem" in the October EA, "The NEC and wiring inside equipment," some control panels are wired to Underwriters Laboratories Standard 508A, "Industrial Control Panels."
section 29.2.1 states: "All internal wiring of power circuits shall have a temperature rating of 90°C minimum. . . ."
Table 29.1, titled "Internal Conductor Ampacity," lists conductors at their 90°C ampacities.
The ampacity for wire pulled in conduit, for instance, is typically based on the 75°C column in NEC Table 310.16. Control panels wired to the UL 508A standard may then use smaller conductor sizes for a given ampacity.
David Bredhold
Application Engineer
Eaton/Cutler-Hammer

## Heat Sinks
|  |  |  | # of Modules | Natural Cooling |  |  | Forced Cooling
| HS Type | Length | Length | n | Rθha |  |  | Rθha
|  | (mm) | (") |  | (°C/W) |  |  | (°C/W)
| P3/120 | 120 | 4.7244 | 1 | 0.55 |  |  | 0.167
|  | 120 | 4.7244 | 2 | 0.53 |  |  | 0.157
|  | 120 | 4.7244 | 3 | 0.43 |  |  | 0.147
| P3/180 | 180 | 7.0866 | 1 | 0.47 |  |  | 0.145
|  | 180 | 7.0866 | 2 | 0.39 |  |  | 0.132
|  | 180 | 7.0866 | 3 | 0.36 |  |  | 0.12
|  | 180 | 7.0866 | 6 | 0.33 |  |  | 0.108
[16 empty] | 115 | 145 | 1.2609
[16 empty] | 140 | 175 | 1.25
[16 empty] | 145 | 180 | 1.2414
[16 empty] | 190 | 260 | 1.3684
[16 empty] | 235 | 315 | 1.3404
[16 empty] | 77 | 100 | 1.2987
|  | Length | Length | n | Rθha |  |  | Rθha | [7 empty] | 250 | 320 | 1.28
|  | (mm) | (") |  | (°C/W) |  |  | (°C/W) | [7 empty] | 325 | 410 | 1.2615
| HS250-6.5 | 165.1 | 6.5 | [14 empty] | 10.3013 | 1.2877
| HS250-10 | 254 | 10 | [15 empty] | 28% plus de courant dans un 3 phases que 2 phases
| HS250-13 | 330.2 | 13
| HS250-15 | 381 | 15
|  | Length | Perimeter | Surface | Volume |  |  |  | HDS
|  | (cm) |  | (cm2) | (cm3) |  |  |  | (cm2)
| HS250-6.5 | 16.51 | 206.2 | 49.6 | 818.896 |  |  | 1 | 3404.362
| HS250-10 | 25.4 | 206.2 | 49.6 | 1259.84 |  |  | 0.45 | 5237.48
| HS250-13 | 33.02 | 206.2 | 49.6 | 1637.792 |  |  | 0.3 | 6808.724
| HS250-15 | 38.1 | 206.2 | 49.6 | 1889.76 |  |  | 0.25 | 7856.22
|  |  |  | # of Modules | Natural Cooling |  |  | Forced Cooling
| HS Type | Length | Length | n | Rθha |  |  | Rθha
|  | (mm) | (") |  | (°C/W) |  |  | (°C/W)
| P3/120 | 120 | 4.7244 | 3 | 0.43 |  |  | 0.147
125
130
135
140
145
150
155
160
|  | 165 | 6.4961 |  | 0.4 |  |  | 0.127
170
175
| P3/180 | 180 | 7.0866 | 3 | 0.36 |  |  | 0.12
185
190
195
|  | 200 | 7.874 |  | 0.31 |  |  | 0.113
205
210
215
220
225
230
235
240
245
|  | 250 | 9.8425 |  | 0.275 |  |  | 0.098
255
260
265
270
275
280
285
290
|  | 295 | [13 empty] | # of Modules | Natural Cooling | Forced Cooling
|  | 300 | 11.811 |  | 0.255 |  |  | 0.088 |  |  |  |  | HS Type | Length | Length | n | Rθha | Rθha
|  | 305 | [11 empty] | (mm) | (") |  | (°C/W) | (°C/W)
|  | 310 | [10 empty] | P3/120 | 120 | 4.7244 | 3 | 0.43 | 0.147
|  | 315 | [11 empty] | 165 | 6.4961 |  | 0.4 | 0.127
|  | 320 | [10 empty] | P3/180 | 180 | 7.0866 | 3 | 0.36 | 0.12
|  | 325 | [11 empty] | 200 | 7.874 |  | 0.31 | 0.113
|  | 330 | 12.9921 |  | 0.2475 | [8 empty] | 250 | 9.8425 |  | 0.275 | 0.098
|  | 335 | [11 empty] | 300 | 11.811 |  | 0.255 | 0.088
|  | 340 | [11 empty] | 330 | 12.9921 |  | 0.2475 | 0.084
|  | 345 | [11 empty] | 380 | 14.9606 |  | 0.24 | 0.08
350
|  | 355 | [13 empty] | # of Modules | Natural Cooling | Forced Cooling
|  | 360 | [10 empty] | HS Type | Length | Length | n | Rθha | Rθha
|  | 365 | [11 empty] | (mm) | (") |  | (°C/W) | (°C/W)
|  | 370 | [10 empty] | Rtheta | 120 | 4.7244 |  | 0.65 | 0.17
|  | 375 | [11 empty] | 165 | 6.4961 |  | 0.58 | 0.15
|  | 380 | 14.9606 |  | 0.24 | [8 empty] | 180 | 7.0866 |  | 0.55 | 0.13
|  | 385 | [11 empty] | 200 | 7.874 |  | 0.48 | 0.117
|  | 390 | [11 empty] | 250 | 9.8425 |  | 0.43 | 0.1
|  | 395 | [11 empty] | 300 | 11.811 |  | 0.36 | 0.09
|  | 400 | [11 empty] | 330 | 12.9921 |  | 0.34 | 0.08
|  | 405 | [11 empty] | 380 | 14.9606 |  | 0.3 | 0.075
|  | 410 | [11 empty] | 400 | 15.748 |  |  | 0.069
415
420
425
430
435
440
445
450
455
460
465
470
475
480
485
490
495
500
|  |  |  | # of Modules | Natural Cooling | Rough formula | Calculator | Tested value 1 | Tested value 2 | Tested value 3 | Forced Cooling | Calculator | Tested value 1 | Tested value 2 | Natural Cooling | Forced Cooling | Natural Cooling | Forced Cooling
HS qty | HS Type | Length | Length | n | Rθha | 50/sqrt(surface) |  |  |  |  | Rθha |  |  |  | Max Power | Max Power | I Max | I Max |  | With BD | With BD |  | Correction factor:x 1.25
|  | (mm) | (") |  | (°C/W) | [5 empty] | (°C/W) |  |  |  | (W) | (W) | (A) | (A)
1 | 1Φ & 3Φ | 165 | 6.4961 |  | 0.58 | 0.51 |  | 0.33 | 0.347 |  | 0.15 | 0.148 |  |  | 129.3103 | 500 | 64.6552 | 250 |  | 43.1034 | 166.6667 | 0.725 | 103.4483 | 400
1 | 1Φ & 3Φ | 250 | 9.8425 |  | 0.43 | 0.41 |  | 0.349 |  |  | 0.1 | 0.108 | 0.108 |  | 174.4186 | 750 | 87.2093 | 375 |  | 58.1395 | 250 | 0.5375 | 139.5349 | 600
1 | 1Φ & 3Φ | 330 | 12.9921 |  | 0.34 | 0.35 |  | 0.209 | 0.254 |  | 0.08 | 0.084 |  |  | 220.5882 | 937.5 | 110.2941 | 468.75 |  | 73.5294 | 312.5 | 0.425 | 176.4706 | 750
1 | 1Φ & 3Φ | 380 | 14.9606 |  | 0.3 | 0.334 |  | 0.236 | 0.23 | 0.276 | 0.075 | 0.079 | 0.074 | 0.072 | 250 | 1000 | 125 | 500 |  | 83.3333 | 333.3333 | 0.375 | 200 | 800
2 | 1Φ | 165 | 6.4961 |  | 0.29 | [5 empty] | 0.075 |  |  |  | 258.6207 | 1000 | 129.3103 | 500 |  |  |  |  | 206.8966 | 800
2 | 1Φ | 250 | 9.8425 |  | 0.215 | [5 empty] | 0.05 |  |  |  | 348.8372 | 1500 | 174.4186 | 750 |  |  |  |  | 279.0698 | 1200
2 | 1Φ | 330 | 12.9921 |  | 0.17 | [5 empty] | 0.04 |  |  |  | 441.1765 | 1875 | 220.5882 | 937.5 |  |  |  |  | 352.9412 | 1500
2 | 1Φ | 380 | 14.9606 |  | 0.15 | [5 empty] | 0.0375 |  |  |  | 500 | 2000 | 250 | 1000 |  |  |  |  | 400 | 1600
3 | 3Φ | 165 | 6.4961 |  | 0.19333 | [5 empty] | 0.05 |  |  |  | 387.931 | 1500 | 193.9655 | 750 |  |  |  |  | 310.3448 | 1200
3 | 3Φ | 250 | 9.8425 |  | 0.14333 | [5 empty] | 0.033333 |  |  |  | 523.2558 | 2250 | 261.6279 | 1125 |  |  |  |  | 418.6047 | 1800
3 | 3Φ | 330 | 12.9921 |  | 0.11333 | [5 empty] | 0.026667 |  |  |  | 661.7647 | 2812.5 | 330.8824 | 1406.25 |  |  |  |  | 529.4118 | 2250
3 | 3Φ | 380 | 14.9606 |  | 0.1 | [5 empty] | 0.025 |  |  |  | 750 | 3000 | 375 | 1500 |  |  |  |  | 600 | 2400
4 | 1Φ | 165 | 6.4961 |  | 0.145 | [5 empty] | 0.0375 |  |  |  | 517.2414 | 2000 | 258.6207 | 1000 |  |  |  |  | 413.7931 | 1600
4 | 1Φ | 250 | 9.8425 |  | 0.1075 | [5 empty] | 0.025 |  |  |  | 697.6744 | 3000 | 348.8372 | 1500 |  |  |  |  | 558.1395 | 2400
4 | 1Φ | 330 | 12.9921 |  | 0.085 | [5 empty] | 0.02 |  |  |  | 882.3529 | 3750 | 441.1765 | 1875 |  |  |  |  | 705.8824 | 3000
4 | 1Φ | 380 | 14.9606 |  | 0.075 | [5 empty] | 0.01875 |  |  |  | 1000 | 4000 | 500 | 2000 |  |  |  |  | 800 | 3200
6 | 3Φ | 165 | 6.4961 |  | 0.096667 | [5 empty] | 0.025 |  |  |  | 775.8621 | 3000 | 387.931 | 1500 |  |  |  |  | 620.6897 | 2400
6 | 3Φ | 250 | 9.8425 |  | 0.071667 | [5 empty] | 0.016667 |  |  |  | 1046.5116 | 4500 | 523.2558 | 2250 |  |  |  |  | 837.2093 | 3600
6 | 3Φ | 330 | 12.9921 |  | 0.056667 | [5 empty] | 0.013333 |  |  |  | 1323.5294 | 5625 | 661.7647 | 2812.5 |  |  |  |  | 1058.8235 | 4500
6 | 3Φ | 380 | 14.9606 |  | 0.05 | [5 empty] | 0.0125 |  |  |  | 1500 | 6000 | 750 | 3000 |  |  |  |  | 1200 | 4800

## Idc Max for SCR-Diod Assemblies
IdcMax | as a fonction of TjMax
HS250 |  | NO FAN | [25 empty] | Equation |  | Solution | Discriminant
3Φ-1Φ-BD-FWD |  |  |  |  | Includes safety factor on Tj |  |  |  |  | Device Parameters | [8 empty] | Operational Conditions | [8 empty] | ax2+bx+c=0 |  | (-b±√(D))/2a
Circuit Type | Total number of devices = n | Number of HS | Number of devices/HS = ns | Number of Modules/HS | IdcMax | IdaveMax | F = Idrms/Idave | IdrmsMax |  | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | HS250 length | Fan | Rθsa | Pd | Pt/HS =nsxPd | Pt =nsxPd | Tj =TjMax-5 | Ts | Ta | a | b | c | D
[5 empty] | (A) | (A) |  | (A) |  |  | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W) | (") |  | (°C/W) | (W) | (W) | (W) | (°C) | (°C) | (°C) | F2rT | VTO | (Ta-Tj)/(Rθjc+Rθcs+nsRθsa) | D = b2-4ac | TOTAL | HS250 | FAN | MODULE | $/(A)
3 | 6 | 1 | 6 | 1 | 29.4852 | 9.8284 | 1.7321 | 17.0233 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 6.5 | N | 0.369 | 16.6071 | 99.6423 | 99.6423 | 120 | 91.768 | 55 | 0.06 | 1.1 | -16.6071 | 5.1957 | 38.85 | 16.35 | 0 | 22.5 | 1.3176
1 | 4 | 1 | 4 | 1 | 25.4419 | 12.721 | 1.4142 | 17.9902 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 6.5 | N | 0.369 | 20.466 | 81.864 | 81.864 | 120 | 85.2078 | 55 | 0.04 | 1.1 | -20.466 | 4.4846 | 38.85 | 16.35 | 0 | 22.5 | 1.527
3 | 6 | 1 | 6 | 1 | 40.6188 | 13.5396 | 1.7321 | 23.4513 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 6.5 | N | 0.369 | 19.0393 | 114.2355 | 114.2355 | 120 | 97.1529 | 55 | 0.03 | 1 | -19.0393 | 3.2847 | 45.15 | 16.35 | 0 | 28.8 | 1.1116
1 | 4 | 1 | 4 | 1 | 35.7788 | 17.8894 | 1.4142 | 25.2994 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 6.5 | N | 0.369 | 24.29 | 97.1599 | 97.1599 | 120 | 90.852 | 55 | 0.02 | 1 | -24.29 | 2.9432 | 45.15 | 16.35 | 0 | 28.8 | 1.2619
1 | 4 | 1 | 4 | 1 | 58.609 | 29.3045 | 1.4142 | 41.4428 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 6.5 | N | 0.369 | 34.6482 | 138.5928 | 138.5928 | 120 | 106.1407 | 55 | 0.011 | 0.86 | -34.6482 | 2.2641 | 40.29 | 16.35 | 0 | 23.94 | 0.68744
3 | 6 | 1 | 6 | 1 | 62.0884 | 20.6961 | 1.7321 | 35.8467 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 6.5 | N | 0.369 | 24.8661 | 149.1966 | 149.1966 | 120 | 110.0536 | 55 | 0.0165 | 0.86 | -24.8661 | 2.3808 | 47.22 | 16.35 | 0 | 30.87 | 0.76053
3 | 6 | 1 | 6 | 3 | 75.4316 | 25.1439 | 1.7321 | 43.5505 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | N | 0.33 | 26.4228 | 158.5366 | 158.5366 | 120 | 107.3171 | 55 | 0.006 | 0.9 | -26.4228 | 1.4441 | 55.35 | 16.35 | 0 | 39 | 0.73378
3 | 6 | 3 | 2 | 1 | 136.489 | 45.4963 | 1.7321 | 78.8019 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | N | 0.369 | 53.3662 | 106.7323 | 320.197 | 120 | 94.3842 | 55 | 0.006 | 0.9 | -53.3662 | 2.0908 | 88.05 | 49.05 | 0 | 39 | 0.64511
1 | 4 | 1 | 4 | 2 | 69.51 | 34.755 | 1.4142 | 49.151 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | N | 0.33 | 36.1111 | 144.4444 | 144.4444 | 120 | 102.6667 | 55 | 0.004 | 0.9 | -36.1111 | 1.3878 | 42.35 | 16.35 | 0 | 26 | 0.60927
1 | 4 | 2 | 2 | 1 | 97.4766 | 48.7383 | 1.4142 | 68.9264 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | N | 0.369 | 53.3662 | 106.7323 | 213.4647 | 120 | 94.3842 | 55 | 0.004 | 0.9 | -53.3662 | 1.6639 | 58.7 | 32.7 | 0 | 26 | 0.6022
3 | 6 | 1 | 6 | 3 | 88.2249 | 29.4083 | 1.7321 | 50.9367 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | N | 0.33 | 28.8889 | 173.3333 | 173.3333 | 120 | 112.2 | 55 | 0.0045 | 0.85 | -28.8889 | 1.2425 | 124.35 | 16.35 | 0 | 108 | 1.4095
3 | 6 | 3 | 2 | 1 | 174.1008 | 58.0336 | 1.7321 | 100.5172 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | N | 0.369 | 64.4841 | 128.9683 | 386.9048 | 120 | 102.5893 | 55 | 0.0045 | 0.85 | -64.4841 | 1.8832 | 157.05 | 49.05 | 0 | 108 | 0.90206
1 | 4 | 1 | 4 | 2 | 83.7976 | 41.8988 | 1.4142 | 59.2538 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | N | 0.33 | 40.8805 | 163.522 | 163.522 | 120 | 108.9623 | 55 | 0.003 | 0.85 | -40.8805 | 1.2131 | 88.35 | 16.35 | 0 | 72 | 1.0543
1 | 4 | 2 | 2 | 1 | 124.4124 | 62.2062 | 1.4142 | 87.9729 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | N | 0.369 | 64.4841 | 128.9683 | 257.9365 | 120 | 102.5893 | 55 | 0.003 | 0.85 | -64.4841 | 1.4963 | 104.7 | 32.7 | 0 | 72 | 0.84156
3 | 6 | 1 | 6 | 3 | 101.7695 | 33.9232 | 1.7321 | 58.7567 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | N | 0.33 | 29.8165 | 178.8991 | 178.8991 | 120 | 114.0367 | 55 | 0.001767 | 0.819 | -29.8165 | 0.8815 | 241.35 | 16.35 | 0 | 225 | 2.3715
3 | 6 | 3 | 2 | 1 | 219.2591 | 73.0864 | 1.7321 | 126.5893 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | N | 0.369 | 69.2964 | 138.5928 | 415.7783 | 120 | 106.1407 | 55 | 0.001767 | 0.819 | -69.2964 | 1.1605 | 274.05 | 49.05 | 0 | 225 | 1.2499
1 | 4 | 1 | 4 | 2 | 97.5799 | 48.79 | 1.4142 | 68.9994 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | N | 0.33 | 42.7632 | 171.0526 | 171.0526 | 120 | 111.4474 | 55 | 0.001178 | 0.819 | -42.7632 | 0.87226 | 166.35 | 16.35 | 0 | 150 | 1.7048
1 | 4 | 2 | 2 | 1 | 152.4973 | 76.2487 | 1.4142 | 107.8319 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | N | 0.369 | 69.2964 | 138.5928 | 277.1855 | 120 | 106.1407 | 55 | 0.001178 | 0.819 | -69.2964 | 0.99729 | 182.7 | 32.7 | 0 | 150 | 1.1981
3 | 6 | 1 | 6 | 3 | 111.6562 | 37.2187 | 1.7321 | 64.4647 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 6.5 | N | 0.33 | 31.477 | 188.862 | 188.862 | 120 | 117.3245 | 55 | 0.00096 | 0.81 | -31.477 | 0.77697 | 421.35 | 16.35 | 0 | 405 | 3.7736
3 | 6 | 3 | 2 | 1 | 264.8122 | 88.2707 | 1.7321 | 152.8894 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 6.5 | N | 0.369 | 78.9793 | 157.9587 | 473.8761 | 120 | 113.2868 | 55 | 0.00096 | 0.81 | -78.9793 | 0.95938 | 454.05 | 49.05 | 0 | 405 | 1.7146
3 | 6 | 1 | 6 | 3 | 130.4591 | 43.4864 | 1.7321 | 75.3206 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 6.5 | N | 0.33 | 31.6148 | 189.6887 | 189.6887 | 120 | 117.5973 | 55 | 0.000552 | 0.703 | -31.6148 | 0.56401 | 991.35 | 16.35 | 0 | 975 | 7.5989
3 | 6 | 3 | 2 | 1 | 314.8233 | 104.9411 | 1.7321 | 181.7633 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 6.5 | N | 0.369 | 79.8526 | 159.7052 | 479.1155 | 120 | 113.9312 | 55 | 0.000552 | 0.703 | -79.8526 | 0.67052 | 1024.05 | 49.05 | 0 | 975 | 3.2528
3 | 6 | 1 | 6 | 6 | 137.4018 | 45.8006 | 1.7321 | 79.329 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | N | 0.33 | 32.2901 | 193.7407 | 193.7407 | 120 | 118.9344 | 55 | 0.000306 | 0.691 | -32.2901 | 0.517 | 1156.35 | 16.35 | 0 | 1140 | 8.4158
3 | 6 | 2 | 3 | 3 | 265.4535 | 88.4845 | 1.7321 | 153.2596 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | N | 0.33 | 63.5386 | 190.6158 | 381.2317 | 120 | 117.9032 | 55 | 0.000306 | 0.691 | -63.5386 | 0.55525 | 1172.7 | 32.7 | 0 | 1140 | 4.4177
3 | 6 | 3 | 2 | 2 | 385.3006 | 128.4335 | 1.7321 | 222.4534 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | N | 0.33 | 93.7951 | 187.5902 | 562.7706 | 120 | 116.9048 | 55 | 0.000306 | 0.691 | -93.7951 | 0.59229 | 1189.05 | 49.05 | 0 | 1140 | 3.086
3 | 6 | 6 | 1 | 1 | 641.2845 | 213.7615 | 1.7321 | 370.2458 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | N | 0.369 | 161.6915 | 161.6915 | 970.1493 | 120 | 114.6642 | 55 | 0.000306 | 0.691 | -161.6915 | 0.67539 | 1238.1 | 98.1 | 0 | 1140 | 1.9307
3 | 6 | 1 | 6 | 1 | 32.8396 | 10.9465 | 1.7321 | 18.9599 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 10 | N | 0.28 | 19.2308 | 115.3846 | 115.3846 | 120 | 87.3077 | 55 | 0.06 | 1.1 | -19.2308 | 5.8254 | 42.36 | 19.86 | 0 | 22.5 | 1.2899
1 | 4 | 1 | 4 | 1 | 27.8282 | 13.9141 | 1.4142 | 19.6775 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 10 | N | 0.28 | 23.0496 | 92.1986 | 92.1986 | 120 | 80.8156 | 55 | 0.04 | 1.1 | -23.0496 | 4.8979 | 42.36 | 19.86 | 0 | 22.5 | 1.5222
3 | 6 | 1 | 6 | 1 | 46.2852 | 15.4284 | 1.7321 | 26.7228 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 10 | N | 0.28 | 22.5694 | 135.4167 | 135.4167 | 120 | 92.9167 | 55 | 0.03 | 1 | -22.5694 | 3.7083 | 48.66 | 19.86 | 0 | 28.8 | 1.0513
1 | 4 | 1 | 4 | 1 | 40.0192 | 20.0096 | 1.4142 | 28.2978 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 10 | N | 0.28 | 28.0172 | 112.069 | 112.069 | 120 | 86.3793 | 55 | 0.02 | 1 | -28.0172 | 3.2414 | 48.66 | 19.86 | 0 | 28.8 | 1.2159
1 | 4 | 1 | 4 | 1 | 69.0005 | 34.5003 | 1.4142 | 48.7907 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 10 | N | 0.28 | 42.7632 | 171.0526 | 171.0526 | 120 | 102.8947 | 55 | 0.011 | 0.86 | -42.7632 | 2.6212 | 43.8 | 19.86 | 0 | 23.94 | 0.63478
3 | 6 | 1 | 6 | 1 | 73.9952 | 24.6651 | 1.7321 | 42.7212 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 10 | N | 0.28 | 31.25 | 187.5 | 187.5 | 120 | 107.5 | 55 | 0.0165 | 0.86 | -31.25 | 2.8021 | 50.73 | 19.86 | 0 | 30.87 | 0.68558
3 | 6 | 1 | 6 | 3 | 93.195 | 31.065 | 1.7321 | 53.8062 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | N | 0.241 | 33.7487 | 202.4922 | 202.4922 | 120 | 103.8006 | 55 | 0.006 | 0.9 | -33.7487 | 1.62 | 58.86 | 19.86 | 0 | 39 | 0.63158
3 | 6 | 3 | 2 | 1 | 154.9671 | 51.6557 | 1.7321 | 89.4703 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | N | 0.28 | 62.5 | 125 | 375 | 120 | 90 | 55 | 0.006 | 0.9 | -62.5 | 2.31 | 98.58 | 59.58 | 0 | 39 | 0.63614
1 | 4 | 1 | 4 | 2 | 84.2553 | 42.1277 | 1.4142 | 59.5775 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | N | 0.241 | 45.0139 | 180.0554 | 180.0554 | 120 | 98.3934 | 55 | 0.004 | 0.9 | -45.0139 | 1.5302 | 45.86 | 19.86 | 0 | 26 | 0.5443
1 | 4 | 2 | 2 | 1 | 111.3406 | 55.6703 | 1.4142 | 78.7297 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | N | 0.28 | 62.5 | 125 | 250 | 120 | 90 | 55 | 0.004 | 0.9 | -62.5 | 1.81 | 65.72 | 39.72 | 0 | 26 | 0.59026
3 | 6 | 1 | 6 | 3 | 111.6798 | 37.2266 | 1.7321 | 64.4783 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | N | 0.241 | 37.8788 | 227.2727 | 227.2727 | 120 | 109.7727 | 55 | 0.0045 | 0.85 | -37.8788 | 1.4043 | 127.86 | 19.86 | 0 | 108 | 1.1449
3 | 6 | 3 | 2 | 1 | 203.3948 | 67.7983 | 1.7321 | 117.43 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | N | 0.28 | 78.3133 | 156.6265 | 469.8795 | 120 | 98.8554 | 55 | 0.0045 | 0.85 | -78.3133 | 2.1321 | 167.58 | 59.58 | 0 | 108 | 0.82391
1 | 4 | 1 | 4 | 2 | 104.623 | 52.3115 | 1.4142 | 73.9796 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | N | 0.241 | 52.6742 | 210.6969 | 210.6969 | 120 | 105.778 | 55 | 0.003 | 0.85 | -52.6742 | 1.3546 | 91.86 | 19.86 | 0 | 72 | 0.87801
1 | 4 | 2 | 2 | 1 | 146.4288 | 73.2144 | 1.4142 | 103.5408 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | N | 0.28 | 78.3133 | 156.6265 | 313.253 | 120 | 98.8554 | 55 | 0.003 | 0.85 | -78.3133 | 1.6623 | 111.72 | 39.72 | 0 | 72 | 0.76296
3 | 6 | 1 | 6 | 3 | 132.1008 | 44.0336 | 1.7321 | 76.2685 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | N | 0.241 | 39.4897 | 236.938 | 236.938 | 120 | 112.1021 | 55 | 0.001767 | 0.819 | -39.4897 | 0.94987 | 244.86 | 19.86 | 0 | 225 | 1.8536
3 | 6 | 3 | 2 | 1 | 263.391 | 87.797 | 1.7321 | 152.0688 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | N | 0.28 | 85.5263 | 171.0526 | 513.1579 | 120 | 102.8947 | 55 | 0.001767 | 0.819 | -85.5263 | 1.2753 | 284.58 | 59.58 | 0 | 225 | 1.0804
1 | 4 | 1 | 4 | 2 | 125.1094 | 62.5547 | 1.4142 | 88.4657 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | N | 0.241 | 55.8419 | 223.3677 | 223.3677 | 120 | 108.8316 | 55 | 0.001178 | 0.819 | -55.8419 | 0.93389 | 169.86 | 19.86 | 0 | 150 | 1.3577
1 | 4 | 2 | 2 | 1 | 184.401 | 92.2005 | 1.4142 | 130.3912 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | N | 0.28 | 85.5263 | 171.0526 | 342.1053 | 120 | 102.8947 | 55 | 0.001178 | 0.819 | -85.5263 | 1.0738 | 189.72 | 39.72 | 0 | 150 | 1.0288
3 | 6 | 1 | 6 | 3 | 148.5287 | 49.5096 | 1.7321 | 85.7531 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 10 | N | 0.241 | 42.4559 | 254.7355 | 254.7355 | 120 | 116.3912 | 55 | 0.00096 | 0.81 | -42.4559 | 0.81913 | 424.86 | 19.86 | 0 | 405 | 2.8605
3 | 6 | 3 | 2 | 1 | 330.1739 | 110.058 | 1.7321 | 190.626 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 10 | N | 0.28 | 100.7752 | 201.5504 | 604.6512 | 120 | 111.4341 | 55 | 0.00096 | 0.81 | -100.7752 | 1.0431 | 464.58 | 59.58 | 0 | 405 | 1.4071
3 | 6 | 1 | 6 | 3 | 174.2974 | 58.0991 | 1.7321 | 100.6306 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 10 | N | 0.241 | 42.707 | 256.2418 | 256.2418 | 120 | 116.7543 | 55 | 0.000552 | 0.703 | -42.707 | 0.58851 | 994.86 | 19.86 | 0 | 975 | 5.7078
3 | 6 | 3 | 2 | 1 | 395.2477 | 131.7492 | 1.7321 | 228.1964 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 10 | N | 0.28 | 102.2013 | 204.4025 | 613.2075 | 120 | 112.2327 | 55 | 0.000552 | 0.703 | -102.2013 | 0.71987 | 1034.58 | 59.58 | 0 | 975 | 2.6175
3 | 6 | 1 | 6 | 6 | 185.7133 | 61.9044 | 1.7321 | 107.2216 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | N | 0.241 | 43.9486 | 263.6917 | 263.6917 | 120 | 118.5497 | 55 | 0.000306 | 0.691 | -43.9486 | 0.53127 | 1159.86 | 19.86 | 0 | 1140 | 6.2454
3 | 6 | 2 | 3 | 3 | 354.7078 | 118.2359 | 1.7321 | 204.7907 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | N | 0.241 | 85.9788 | 257.9365 | 515.873 | 120 | 117.1627 | 55 | 0.000306 | 0.691 | -85.9788 | 0.58272 | 1179.72 | 39.72 | 0 | 1140 | 3.3259
3 | 6 | 3 | 2 | 2 | 509.6234 | 169.8745 | 1.7321 | 294.2312 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | N | 0.241 | 126.2136 | 252.4272 | 757.2816 | 120 | 115.835 | 55 | 0.000306 | 0.691 | -126.2136 | 0.63197 | 1199.58 | 59.58 | 0 | 1140 | 2.3539
3 | 6 | 6 | 1 | 1 | 805.7596 | 268.5865 | 1.7321 | 465.2055 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | N | 0.28 | 207.6677 | 207.6677 | 1246.0064 | 120 | 113.147 | 55 | 0.000306 | 0.691 | -207.6677 | 0.73167 | 1259.16 | 119.16 | 0 | 1140 | 1.5627
3 | 6 | 1 | 6 | 1 | 33.9396 | 11.3132 | 1.7321 | 19.595 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 13 | N | 0.255 | 20.1238 | 120.743 | 120.743 | 120 | 85.7895 | 55 | 0.06 | 1.1 | -20.1238 | 6.0397 | 47.05 | 24.55 | 0 | 22.5 | 1.3863
1 | 4 | 1 | 4 | 1 | 28.5888 | 14.2944 | 1.4142 | 20.2153 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 13 | N | 0.255 | 23.8971 | 95.5882 | 95.5882 | 120 | 79.375 | 55 | 0.04 | 1.1 | -23.8971 | 5.0335 | 47.05 | 24.55 | 0 | 22.5 | 1.6457
3 | 6 | 1 | 6 | 1 | 48.1981 | 16.066 | 1.7321 | 27.8272 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 13 | N | 0.255 | 23.8095 | 142.8571 | 142.8571 | 120 | 91.4286 | 55 | 0.03 | 1 | -23.8095 | 3.8571 | 53.35 | 24.55 | 0 | 28.8 | 1.1069
1 | 4 | 1 | 4 | 1 | 41.4104 | 20.7052 | 1.4142 | 29.2816 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 13 | N | 0.255 | 29.2793 | 117.1171 | 117.1171 | 120 | 84.8649 | 55 | 0.02 | 1 | -29.2793 | 3.3423 | 53.35 | 24.55 | 0 | 28.8 | 1.2883
1 | 4 | 1 | 4 | 1 | 72.6748 | 36.3374 | 1.4142 | 51.3889 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 13 | N | 0.255 | 45.7746 | 183.0986 | 183.0986 | 120 | 101.6901 | 55 | 0.011 | 0.86 | -45.7746 | 2.7537 | 48.49 | 24.55 | 0 | 23.94 | 0.66722
3 | 6 | 1 | 6 | 1 | 78.2874 | 26.0958 | 1.7321 | 45.1993 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 13 | N | 0.255 | 33.6788 | 202.0725 | 202.0725 | 120 | 106.5285 | 55 | 0.0165 | 0.86 | -33.6788 | 2.9624 | 55.42 | 24.55 | 0 | 30.87 | 0.7079
3 | 6 | 1 | 6 | 3 | 98.7154 | 32.9051 | 1.7321 | 56.9934 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | N | 0.22 | 36.1111 | 216.6667 | 216.6667 | 120 | 102.6667 | 55 | 0.006 | 0.9 | -36.1111 | 1.6767 | 63.55 | 24.55 | 0 | 39 | 0.64377
3 | 6 | 3 | 2 | 1 | 161.1474 | 53.7158 | 1.7321 | 93.0385 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | N | 0.255 | 65.6566 | 131.3131 | 393.9394 | 120 | 88.4848 | 55 | 0.006 | 0.9 | -65.6566 | 2.3858 | 112.65 | 73.65 | 0 | 39 | 0.69905
1 | 4 | 1 | 4 | 2 | 88.7182 | 44.3591 | 1.4142 | 62.7333 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | N | 0.22 | 47.7941 | 191.1765 | 191.1765 | 120 | 97.0588 | 55 | 0.004 | 0.9 | -47.7941 | 1.5747 | 50.55 | 24.55 | 0 | 26 | 0.56978
1 | 4 | 2 | 2 | 1 | 116.0008 | 58.0004 | 1.4142 | 82.025 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | N | 0.255 | 65.6566 | 131.3131 | 262.6263 | 120 | 88.4848 | 55 | 0.004 | 0.9 | -65.6566 | 1.8605 | 75.1 | 49.1 | 0 | 26 | 0.64741
3 | 6 | 1 | 6 | 3 | 119.2071 | 39.7357 | 1.7321 | 68.8242 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | N | 0.22 | 40.8805 | 245.283 | 245.283 | 120 | 108.9623 | 55 | 0.0045 | 0.85 | -40.8805 | 1.4583 | 132.55 | 24.55 | 0 | 108 | 1.1119
3 | 6 | 3 | 2 | 1 | 213.6017 | 71.2006 | 1.7321 | 123.323 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | N | 0.255 | 83.3333 | 166.6667 | 500 | 120 | 97.5 | 55 | 0.0045 | 0.85 | -83.3333 | 2.2225 | 181.65 | 73.65 | 0 | 108 | 0.85041
1 | 4 | 1 | 4 | 2 | 111.1791 | 55.5896 | 1.4142 | 78.6155 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | N | 0.22 | 56.5217 | 226.087 | 226.087 | 120 | 104.7391 | 55 | 0.003 | 0.85 | -56.5217 | 1.4008 | 96.55 | 24.55 | 0 | 72 | 0.86842
1 | 4 | 2 | 2 | 1 | 154.1468 | 77.0734 | 1.4142 | 108.9983 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | N | 0.255 | 83.3333 | 166.6667 | 333.3333 | 120 | 97.5 | 55 | 0.003 | 0.85 | -83.3333 | 1.7225 | 121.1 | 49.1 | 0 | 72 | 0.78561
3 | 6 | 1 | 6 | 3 | 142.1165 | 47.3722 | 1.7321 | 82.051 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | N | 0.22 | 42.7632 | 256.5789 | 256.5789 | 120 | 111.4474 | 55 | 0.001767 | 0.819 | -42.7632 | 0.97301 | 249.55 | 24.55 | 0 | 225 | 1.756
3 | 6 | 3 | 2 | 1 | 279.2601 | 93.0867 | 1.7321 | 161.2309 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | N | 0.255 | 91.5493 | 183.0986 | 549.2958 | 120 | 101.6901 | 55 | 0.001767 | 0.819 | -91.5493 | 1.3178 | 298.65 | 73.65 | 0 | 225 | 1.0694
1 | 4 | 1 | 4 | 2 | 134.0494 | 67.0247 | 1.4142 | 94.7873 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | N | 0.22 | 60.1852 | 240.7407 | 240.7407 | 120 | 107.963 | 55 | 0.001178 | 0.819 | -60.1852 | 0.95435 | 174.55 | 24.55 | 0 | 150 | 1.3021
1 | 4 | 2 | 2 | 1 | 195.9501 | 97.975 | 1.4142 | 138.5576 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | N | 0.255 | 91.5493 | 183.0986 | 366.1972 | 120 | 101.6901 | 55 | 0.001178 | 0.819 | -91.5493 | 1.1021 | 199.1 | 49.1 | 0 | 150 | 1.0161
3 | 6 | 1 | 6 | 3 | 161.0934 | 53.6978 | 1.7321 | 93.0073 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 13 | N | 0.22 | 46.2633 | 277.5801 | 277.5801 | 120 | 116.0676 | 55 | 0.00096 | 0.81 | -46.2633 | 0.83375 | 429.55 | 24.55 | 0 | 405 | 2.6665
3 | 6 | 3 | 2 | 1 | 354.8584 | 118.2861 | 1.7321 | 204.8776 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 13 | N | 0.255 | 109.2437 | 218.4874 | 655.4622 | 120 | 110.7143 | 55 | 0.00096 | 0.81 | -109.2437 | 1.0756 | 478.65 | 73.65 | 0 | 405 | 1.3488
13
3 | 6 | 1 | 6 | 3 | 189.3173 | 63.1058 | 1.7321 | 109.3024 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 13 | N | 0.22 | 46.5616 | 279.3696 | 279.3696 | 120 | 116.4613 | 55 | 0.000552 | 0.703 | -46.5616 | 0.59702 | 999.55 | 24.55 | 0 | 975 | 5.2798
3 | 6 | 3 | 2 | 1 | 425.8778 | 141.9593 | 1.7321 | 245.8807 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 13 | N | 0.255 | 110.9215 | 221.843 | 665.529 | 120 | 111.57 | 55 | 0.000552 | 0.703 | -110.9215 | 0.73912 | 1048.65 | 73.65 | 0 | 975 | 2.4623
3 | 6 | 1 | 6 | 6 | 202.5192 | 67.5064 | 1.7321 | 116.9245 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | N | 0.22 | 48.0414 | 288.2483 | 288.2483 | 120 | 118.4146 | 55 | 0.000306 | 0.691 | -48.0414 | 0.53628 | 1164.55 | 24.55 | 0 | 1140 | 5.7503
3 | 6 | 2 | 3 | 3 | 385.3006 | 128.4335 | 1.7321 | 222.4534 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | N | 0.22 | 93.7951 | 281.3853 | 562.7706 | 120 | 116.9048 | 55 | 0.000306 | 0.691 | -93.7951 | 0.59229 | 1189.1 | 49.1 | 0 | 1140 | 3.0862
3 | 6 | 3 | 2 | 2 | 551.6893 | 183.8964 | 1.7321 | 318.518 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | N | 0.22 | 137.4207 | 274.8414 | 824.5243 | 120 | 115.4651 | 55 | 0.000306 | 0.691 | -137.4207 | 0.64568 | 1213.65 | 73.65 | 0 | 1140 | 2.1999
3 | 6 | 6 | 1 | 1 | 868.5138 | 289.5046 | 1.7321 | 501.4367 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | N | 0.255 | 225.6944 | 225.6944 | 1354.1667 | 120 | 112.5521 | 55 | 0.000306 | 0.691 | -225.6944 | 0.75373 | 1287.3 | 147.3 | 0 | 1140 | 1.4822
3 | 6 | 1 | 6 | 1 | 34.1695 | 11.3898 | 1.7321 | 19.7278 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 15 | N | 0.25 | 20.3125 | 121.875 | 121.875 | 120 | 85.4688 | 55 | 0.06 | 1.1 | -20.3125 | 6.085 | 50.76 | 28.26 | 0 | 22.5 | 1.4855
1 | 4 | 1 | 4 | 1 | 28.7464 | 14.3732 | 1.4142 | 20.3268 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 15 | N | 0.25 | 24.0741 | 96.2963 | 96.2963 | 120 | 79.0741 | 55 | 0.04 | 1.1 | -24.0741 | 5.0619 | 50.76 | 28.26 | 0 | 22.5 | 1.7658
3 | 6 | 1 | 6 | 1 | 48.6013 | 16.2004 | 1.7321 | 28.06 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 15 | N | 0.25 | 24.0741 | 144.4444 | 144.4444 | 120 | 91.1111 | 55 | 0.03 | 1 | -24.0741 | 3.8889 | 57.06 | 28.26 | 0 | 28.8 | 1.174
1 | 4 | 1 | 4 | 1 | 41.7011 | 20.8505 | 1.4142 | 29.4871 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 15 | N | 0.25 | 29.5455 | 118.1818 | 118.1818 | 120 | 84.5455 | 55 | 0.02 | 1 | -29.5455 | 3.3636 | 57.06 | 28.26 | 0 | 28.8 | 1.3683
1 | 4 | 1 | 4 | 1 | 73.4609 | 36.7304 | 1.4142 | 51.9447 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 15 | N | 0.25 | 46.4286 | 185.7143 | 185.7143 | 120 | 101.4286 | 55 | 0.011 | 0.86 | -46.4286 | 2.7825 | 52.2 | 28.26 | 0 | 23.94 | 0.71058
3 | 6 | 1 | 6 | 1 | 79.2116 | 26.4039 | 1.7321 | 45.7328 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 15 | N | 0.25 | 34.2105 | 205.2632 | 205.2632 | 120 | 106.3158 | 55 | 0.0165 | 0.86 | -34.2105 | 2.9975 | 59.13 | 28.26 | 0 | 30.87 | 0.74648
3 | 6 | 1 | 6 | 3 | 101.5876 | 33.8625 | 1.7321 | 58.6516 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | N | 0.21 | 37.3563 | 224.1379 | 224.1379 | 120 | 102.069 | 55 | 0.006 | 0.9 | -37.3563 | 1.7066 | 67.26 | 28.26 | 0 | 39 | 0.66209
3 | 6 | 3 | 2 | 1 | 162.4465 | 54.1488 | 1.7321 | 93.7885 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | N | 0.25 | 66.3265 | 132.6531 | 397.9592 | 120 | 88.1633 | 55 | 0.006 | 0.9 | -66.3265 | 2.4018 | 123.78 | 84.78 | 0 | 39 | 0.76197
1 | 4 | 1 | 4 | 2 | 91.0181 | 45.509 | 1.4142 | 64.3595 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | N | 0.21 | 49.2424 | 196.9697 | 196.9697 | 120 | 96.3636 | 55 | 0.004 | 0.9 | -49.2424 | 1.5979 | 54.26 | 28.26 | 0 | 26 | 0.59615
1 | 4 | 2 | 2 | 1 | 116.9818 | 58.4909 | 1.4142 | 82.7186 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | N | 0.25 | 66.3265 | 132.6531 | 265.3061 | 120 | 88.1633 | 55 | 0.004 | 0.9 | -66.3265 | 1.8712 | 82.52 | 56.52 | 0 | 26 | 0.70541
3 | 6 | 1 | 6 | 3 | 123.1702 | 41.0567 | 1.7321 | 71.1123 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | N | 0.21 | 42.4837 | 254.902 | 254.902 | 120 | 108.5294 | 55 | 0.0045 | 0.85 | -42.4837 | 1.4872 | 136.26 | 28.26 | 0 | 108 | 1.1063
3 | 6 | 3 | 2 | 1 | 215.7748 | 71.9249 | 1.7321 | 124.5776 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | N | 0.25 | 84.4156 | 168.8312 | 506.4935 | 120 | 97.2078 | 55 | 0.0045 | 0.85 | -84.4156 | 2.242 | 192.78 | 84.78 | 0 | 108 | 0.89343
1 | 4 | 1 | 4 | 2 | 114.6062 | 57.3031 | 1.4142 | 81.0388 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | N | 0.21 | 58.5586 | 234.2342 | 234.2342 | 120 | 104.1892 | 55 | 0.003 | 0.85 | -58.5586 | 1.4252 | 100.26 | 28.26 | 0 | 72 | 0.87482
1 | 4 | 2 | 2 | 1 | 155.7929 | 77.8965 | 1.4142 | 110.1622 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | N | 0.25 | 84.4156 | 168.8312 | 337.6623 | 120 | 97.2078 | 55 | 0.003 | 0.85 | -84.4156 | 1.7355 | 128.52 | 56.52 | 0 | 72 | 0.82494
3 | 6 | 1 | 6 | 3 | 147.4443 | 49.1481 | 1.7321 | 85.127 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | N | 0.21 | 44.5205 | 267.1233 | 267.1233 | 120 | 111.0959 | 55 | 0.001767 | 0.819 | -44.5205 | 0.98543 | 253.26 | 28.26 | 0 | 225 | 1.7177
3 | 6 | 3 | 2 | 1 | 282.6719 | 94.224 | 1.7321 | 163.2007 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | N | 0.25 | 92.8571 | 185.7143 | 557.1429 | 120 | 101.4286 | 55 | 0.001767 | 0.819 | -92.8571 | 1.3271 | 309.78 | 84.78 | 0 | 225 | 1.0959
1 | 4 | 1 | 4 | 2 | 138.775 | 69.3875 | 1.4142 | 98.1288 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | N | 0.21 | 62.5 | 250 | 250 | 120 | 107.5 | 55 | 0.001178 | 0.819 | -62.5 | 0.96526 | 178.26 | 28.26 | 0 | 150 | 1.2845
1 | 4 | 2 | 2 | 1 | 198.4381 | 99.2191 | 1.4142 | 140.3169 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | N | 0.25 | 92.8571 | 185.7143 | 371.4286 | 120 | 101.4286 | 55 | 0.001178 | 0.819 | -92.8571 | 1.1083 | 206.52 | 56.52 | 0 | 150 | 1.0407
3 | 6 | 1 | 6 | 3 | 167.858 | 55.9527 | 1.7321 | 96.9129 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | N | 0.21 | 48.3271 | 289.9628 | 289.9628 | 120 | 115.8922 | 55 | 0.00096 | 0.81 | -48.3271 | 0.84168 | 433.26 | 28.26 | 0 | 405 | 2.5811
3 | 6 | 3 | 2 | 1 | 360.2512 | 120.0837 | 1.7321 | 207.9911 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | N | 0.25 | 111.1111 | 222.2222 | 666.6667 | 120 | 110.5556 | 55 | 0.00096 | 0.81 | -111.1111 | 1.0828 | 489.78 | 84.78 | 0 | 405 | 1.3596
3 | 6 | 1 | 6 | 3 | 197.4206 | 65.8069 | 1.7321 | 113.9809 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | N | 0.21 | 48.6527 | 291.9162 | 291.9162 | 120 | 116.3024 | 55 | 0.000552 | 0.703 | -48.6527 | 0.60163 | 1003.26 | 28.26 | 0 | 975 | 5.0818
3 | 6 | 3 | 2 | 1 | 432.5879 | 144.196 | 1.7321 | 249.7548 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | N | 0.25 | 112.8472 | 225.6944 | 677.0833 | 120 | 111.4236 | 55 | 0.000552 | 0.703 | -112.8472 | 0.74338 | 1059.78 | 84.78 | 0 | 975 | 2.4499
3 | 6 | 1 | 6 | 6 | 211.6401 | 70.5467 | 1.7321 | 122.1905 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.21 | 50.2707 | 301.6241 | 301.6241 | 120 | 118.3411 | 55 | 0.000306 | 0.691 | -50.2707 | 0.53901 | 1168.26 | 28.26 | 0 | 1140 | 5.52
3 | 6 | 2 | 3 | 3 | 401.8086 | 133.9362 | 1.7321 | 231.9843 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.21 | 98.0392 | 294.1176 | 588.2353 | 120 | 116.7647 | 55 | 0.000306 | 0.691 | -98.0392 | 0.59748 | 1196.52 | 56.52 | 0 | 1140 | 2.9778
3 | 6 | 3 | 2 | 2 | 574.276 | 191.4253 | 1.7321 | 331.5584 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.21 | 143.4879 | 286.9757 | 860.9272 | 120 | 115.2649 | 55 | 0.000306 | 0.691 | -143.4879 | 0.65311 | 1224.78 | 84.78 | 0 | 1140 | 2.1327
3 | 6 | 6 | 1 | 1 | 882.2706 | 294.0902 | 1.7321 | 509.3792 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.25 | 229.682 | 229.682 | 1378.0919 | 120 | 112.4205 | 55 | 0.000306 | 0.691 | -229.682 | 0.75861 | 1309.56 | 169.56 | 0 | 1140 | 1.4843
HS250 | [27 empty] | Equation |  | Solution | Discriminant
3Φ-1Φ-BD-FWD |  |  |  |  | Includes safety factor on Tj |  |  |  |  | Device Parameters | [8 empty] | Operational Conditions | [8 empty] | ax2+bx+c=0 |  | (-b±√(D))/2a
Circuit Type | Total number of devices = n | Number of HS | Number of devices/HS = ns | Number of Modules/HS | IdcMax | IdaveMax | F = Idrms/Idave | IdrmsMax |  | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | HS250 length | Fan | Rθsa | Pd | Pt/HS =nsxPd | Pt =nsxPd | Tj =TjMax-5 | Ts | Ta | a | b | c | D
[5 empty] | (A) | (A) |  | (A) |  |  | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W) | (") |  | (°C/W) | (W) | (W) | (W) | (°C) | (°C) | (°C) | F2rT | VTO | (Ta-Tj)/(Rθjc+Rθcs+nsRθsa) | D = b2-4ac
3 | 6 | 1 | 6 | 1 | 41.5311 | 13.8437 | 1.7321 | 23.978 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 6.5 | Y | 0.122 | 26.727 | 160.3618 | 160.3618 | 120 | 74.5641 | 55 | 0.06 | 1.1 | -26.727 | 7.6245 | 50.85 | 16.35 | 12 | 22.5 | 1.2244
1 | 4 | 1 | 4 | 1 | 33.5492 | 16.7746 | 1.4142 | 23.7228 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 6.5 | Y | 0.122 | 29.7075 | 118.83 | 118.83 | 120 | 69.4973 | 55 | 0.04 | 1.1 | -29.7075 | 5.9632 | 50.85 | 16.35 | 12 | 22.5 | 1.5157
3 | 6 | 1 | 6 | 1 | 62.2193 | 20.7398 | 1.7321 | 35.9223 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 6.5 | Y | 0.122 | 33.6439 | 201.8634 | 201.8634 | 120 | 79.6273 | 55 | 0.03 | 1 | -33.6439 | 5.0373 | 57.15 | 16.35 | 12 | 28.8 | 0.91853
1 | 4 | 1 | 4 | 1 | 51.0021 | 25.501 | 1.4142 | 36.0639 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 6.5 | Y | 0.122 | 38.5071 | 154.0284 | 154.0284 | 120 | 73.7915 | 55 | 0.02 | 1 | -38.5071 | 4.0806 | 57.15 | 16.35 | 12 | 28.8 | 1.1205
1 | 4 | 1 | 4 | 1 | 102.7323 | 51.3662 | 1.4142 | 72.6427 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 6.5 | Y | 0.122 | 73.1982 | 292.7928 | 292.7928 | 120 | 90.7207 | 55 | 0.011 | 0.86 | -73.1982 | 3.9603 | 52.29 | 16.35 | 12 | 23.94 | 0.50899
3 | 6 | 1 | 6 | 1 | 115.2934 | 38.4311 | 1.7321 | 66.5647 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 6.5 | Y | 0.122 | 57.4205 | 344.523 | 344.523 | 120 | 97.0318 | 55 | 0.0165 | 0.86 | -57.4205 | 4.5294 | 59.22 | 16.35 | 12 | 30.87 | 0.51365
3 | 6 | 1 | 6 | 3 | 141.5895 | 47.1965 | 1.7321 | 81.7468 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | Y | 0.114 | 55.8419 | 335.0515 | 335.0515 | 120 | 93.1959 | 55 | 0.006 | 0.9 | -55.8419 | 2.1502 | 67.35 | 16.35 | 12 | 39 | 0.47567
3 | 6 | 3 | 2 | 1 | 205.4573 | 68.4858 | 1.7321 | 118.6208 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | Y | 0.122 | 89.779 | 179.558 | 538.674 | 120 | 76.9061 | 55 | 0.006 | 0.9 | -89.779 | 2.9647 | 124.05 | 49.05 | 36 | 39 | 0.60378
1 | 4 | 1 | 4 | 2 | 121.5104 | 60.7552 | 1.4142 | 85.9208 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | Y | 0.114 | 69.4444 | 277.7778 | 277.7778 | 120 | 86.6667 | 55 | 0.004 | 0.9 | -69.4444 | 1.9211 | 54.35 | 16.35 | 12 | 26 | 0.44729
1 | 4 | 2 | 2 | 1 | 149.7052 | 74.8526 | 1.4142 | 105.8576 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | Y | 0.122 | 89.779 | 179.558 | 359.116 | 120 | 76.9061 | 55 | 0.004 | 0.9 | -89.779 | 2.2465 | 82.7 | 32.7 | 24 | 26 | 0.55242
3 | 6 | 1 | 6 | 3 | 182.0118 | 60.6706 | 1.7321 | 105.0846 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | Y | 0.114 | 68.1342 | 408.805 | 408.805 | 120 | 101.6038 | 55 | 0.0045 | 0.85 | -68.1342 | 1.9489 | 136.35 | 16.35 | 12 | 108 | 0.74913
3 | 6 | 3 | 2 | 1 | 293.898 | 97.966 | 1.7321 | 169.6821 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | Y | 0.122 | 126.4591 | 252.9183 | 758.7549 | 120 | 85.856 | 55 | 0.0045 | 0.85 | -126.4591 | 2.9988 | 193.05 | 49.05 | 36 | 108 | 0.65686
1 | 4 | 1 | 4 | 2 | 163.4925 | 81.7463 | 1.4142 | 115.6067 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | Y | 0.114 | 89.5317 | 358.1267 | 358.1267 | 120 | 95.8264 | 55 | 0.003 | 0.85 | -89.5317 | 1.7969 | 100.35 | 16.35 | 12 | 72 | 0.61379
1 | 4 | 2 | 2 | 1 | 215.5554 | 107.7777 | 1.4142 | 152.4207 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 6.5 | Y | 0.122 | 126.4591 | 252.9183 | 505.8366 | 120 | 85.856 | 55 | 0.003 | 0.85 | -126.4591 | 2.24 | 128.7 | 32.7 | 24 | 72 | 0.59706
3 | 6 | 1 | 6 | 3 | 230.9721 | 76.9907 | 1.7321 | 133.3518 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | Y | 0.114 | 73.5294 | 441.1765 | 441.1765 | 120 | 105.2941 | 55 | 0.001767 | 0.819 | -73.5294 | 1.1905 | 253.35 | 16.35 | 12 | 225 | 1.0969
3 | 6 | 3 | 2 | 1 | 413.3654 | 137.7885 | 1.7321 | 238.6566 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | Y | 0.122 | 146.3964 | 292.7928 | 878.3784 | 120 | 90.7207 | 55 | 0.001767 | 0.819 | -146.3964 | 1.7055 | 310.05 | 49.05 | 36 | 225 | 0.75006
1 | 4 | 1 | 4 | 2 | 210.193 | 105.0965 | 1.4142 | 148.6289 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | Y | 0.114 | 99.0854 | 396.3415 | 396.3415 | 120 | 100.1829 | 55 | 0.001178 | 0.819 | -99.0854 | 1.1377 | 178.35 | 16.35 | 12 | 150 | 0.84851
1 | 4 | 2 | 2 | 1 | 294.94 | 147.47 | 1.4142 | 208.5541 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 6.5 | Y | 0.122 | 146.3964 | 292.7928 | 585.5856 | 120 | 90.7207 | 55 | 0.001178 | 0.819 | -146.3964 | 1.3606 | 206.7 | 32.7 | 24 | 150 | 0.70082
3 | 6 | 1 | 6 | 3 | 281.7056 | 93.9019 | 1.7321 | 162.6428 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 6.5 | Y | 0.114 | 84.5254 | 507.1521 | 507.1521 | 120 | 112.8153 | 55 | 0.00096 | 0.81 | -84.5254 | 0.98068 | 433.35 | 16.35 | 12 | 405 | 1.5383
3 | 6 | 3 | 2 | 1 | 592.8718 | 197.6239 | 1.7321 | 342.2947 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 6.5 | Y | 0.122 | 197.5684 | 395.1368 | 1185.4103 | 120 | 103.2067 | 55 | 0.00096 | 0.81 | -197.5684 | 1.4148 | 490.05 | 49.05 | 36 | 405 | 0.82657
3 | 6 | 1 | 6 | 3 | 335.5137 | 111.8379 | 1.7321 | 193.709 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 6.5 | Y | 0.114 | 85.5263 | 513.1579 | 513.1579 | 120 | 113.5 | 55 | 0.000552 | 0.703 | -85.5263 | 0.68305 | 1003.35 | 16.35 | 12 | 975 | 2.9905
3 | 6 | 3 | 2 | 1 | 728.0762 | 242.6921 | 1.7321 | 420.355 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 6.5 | Y | 0.122 | 203.125 | 406.25 | 1218.75 | 120 | 104.5625 | 55 | 0.000552 | 0.703 | -203.125 | 0.94271 | 1060.05 | 49.05 | 36 | 975 | 1.456
3 | 6 | 1 | 6 | 6 | 373.0422 | 124.3474 | 1.7321 | 215.376 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | Y | 0.114 | 90.6555 | 543.9331 | 543.9331 | 120 | 117.0084 | 55 | 0.000306 | 0.691 | -90.6555 | 0.58844 | 1168.35 | 16.35 | 12 | 1140 | 3.132
3 | 6 | 2 | 3 | 3 | 683.5601 | 227.8534 | 1.7321 | 394.6536 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | Y | 0.114 | 173.3333 | 520 | 1040 | 120 | 114.28 | 55 | 0.000306 | 0.691 | -173.3333 | 0.68964 | 1196.7 | 32.7 | 24 | 1140 | 1.7507
3 | 6 | 3 | 2 | 2 | 948.4417 | 316.1472 | 1.7321 | 547.5831 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | Y | 0.114 | 249.0421 | 498.0843 | 1494.2529 | 120 | 111.7816 | 55 | 0.000306 | 0.691 | -249.0421 | 0.78231 | 1225.05 | 49.05 | 36 | 1140 | 1.2916
3 | 6 | 6 | 1 | 1 | 1492.0341 | 497.3447 | 1.7321 | 861.4263 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 6.5 | Y | 0.122 | 419.3548 | 419.3548 | 2516.129 | 120 | 106.1613 | 55 | 0.000306 | 0.691 | -419.3548 | 0.99077 | 1310.1 | 98.1 | 72 | 1140 | 0.87806
3 | 6 | 1 | 6 | 1 | 42.0395 | 14.0132 | 1.7321 | 24.2715 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 10 | Y | 0.115 | 27.1967 | 163.1799 | 163.1799 | 120 | 73.7657 | 55 | 0.06 | 1.1 | -27.1967 | 7.7372 | 54.36 | 19.86 | 12 | 22.5 | 1.2931
1 | 4 | 1 | 4 | 1 | 33.8637 | 16.9319 | 1.4142 | 23.9453 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 10 | Y | 0.115 | 30.0926 | 120.3704 | 120.3704 | 120 | 68.8426 | 55 | 0.04 | 1.1 | -30.0926 | 6.0248 | 54.36 | 19.86 | 12 | 22.5 | 1.6053
3 | 6 | 1 | 6 | 1 | 63.2142 | 21.0714 | 1.7321 | 36.4967 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 10 | Y | 0.115 | 34.3915 | 206.3492 | 206.3492 | 120 | 78.7302 | 55 | 0.03 | 1 | -34.3915 | 5.127 | 60.66 | 19.86 | 12 | 28.8 | 0.95959
1 | 4 | 1 | 4 | 1 | 51.6431 | 25.8216 | 1.4142 | 36.5172 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 10 | Y | 0.115 | 39.1566 | 156.6265 | 156.6265 | 120 | 73.012 | 55 | 0.02 | 1 | -39.1566 | 4.1325 | 60.66 | 19.86 | 12 | 28.8 | 1.1746
1 | 4 | 1 | 4 | 1 | 105.1118 | 52.5559 | 1.4142 | 74.3252 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 10 | Y | 0.115 | 75.5814 | 302.3256 | 302.3256 | 120 | 89.7674 | 55 | 0.011 | 0.86 | -75.5814 | 4.0652 | 55.8 | 19.86 | 12 | 23.94 | 0.53086
3 | 6 | 1 | 6 | 1 | 118.3875 | 39.4625 | 1.7321 | 68.3511 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 10 | Y | 0.115 | 59.633 | 357.7982 | 357.7982 | 120 | 96.1468 | 55 | 0.0165 | 0.86 | -59.633 | 4.6754 | 62.73 | 19.86 | 12 | 30.87 | 0.52987
3 | 6 | 1 | 6 | 3 | 151.0414 | 50.3471 | 1.7321 | 87.2038 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.099 | 60.5214 | 363.1285 | 363.1285 | 120 | 90.9497 | 55 | 0.006 | 0.9 | -60.5214 | 2.2625 | 70.86 | 19.86 | 12 | 39 | 0.46914
3 | 6 | 3 | 2 | 1 | 208.5308 | 69.5103 | 1.7321 | 120.3953 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.115 | 91.5493 | 183.0986 | 549.2958 | 120 | 76.0563 | 55 | 0.006 | 0.9 | -91.5493 | 3.0072 | 134.58 | 59.58 | 36 | 39 | 0.64537
1 | 4 | 1 | 4 | 2 | 128.3071 | 64.1536 | 1.4142 | 90.7268 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.099 | 74.2009 | 296.8037 | 296.8037 | 120 | 84.3836 | 55 | 0.004 | 0.9 | -74.2009 | 1.9972 | 57.86 | 19.86 | 12 | 26 | 0.45095
1 | 4 | 2 | 2 | 1 | 152.0601 | 76.03 | 1.4142 | 107.5227 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.115 | 91.5493 | 183.0986 | 366.1972 | 120 | 76.0563 | 55 | 0.004 | 0.9 | -91.5493 | 2.2748 | 89.72 | 39.72 | 24 | 26 | 0.59003
3 | 6 | 1 | 6 | 3 | 197.0215 | 65.6738 | 1.7321 | 113.7504 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | Y | 0.099 | 75.2315 | 451.3889 | 451.3889 | 120 | 99.6875 | 55 | 0.0045 | 0.85 | -75.2315 | 2.0767 | 139.86 | 19.86 | 12 | 108 | 0.70987
3 | 6 | 3 | 2 | 1 | 300 | 100 | 1.7321 | 173.2051 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | Y | 0.115 | 130 | 260 | 780 | 120 | 84.9 | 55 | 0.0045 | 0.85 | -130 | 3.0625 | 203.58 | 59.58 | 36 | 108 | 0.6786
1 | 4 | 1 | 4 | 2 | 175.3691 | 87.6845 | 1.4142 | 124.0047 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | Y | 0.099 | 97.5976 | 390.3904 | 390.3904 | 120 | 93.6486 | 55 | 0.003 | 0.85 | -97.5976 | 1.8937 | 103.86 | 19.86 | 12 | 72 | 0.59224
1 | 4 | 2 | 2 | 1 | 220.2648 | 110.1324 | 1.4142 | 155.7508 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 10 | Y | 0.115 | 130 | 260 | 520 | 120 | 84.9 | 55 | 0.003 | 0.85 | -130 | 2.2825 | 135.72 | 39.72 | 24 | 72 | 0.61617
3 | 6 | 1 | 6 | 3 | 253.6118 | 84.5373 | 1.7321 | 146.4228 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | Y | 0.099 | 81.864 | 491.1839 | 491.1839 | 120 | 103.6272 | 55 | 0.001767 | 0.819 | -81.864 | 1.2494 | 256.86 | 19.86 | 12 | 225 | 1.0128
3 | 6 | 3 | 2 | 1 | 424.2611 | 141.4204 | 1.7321 | 244.9473 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | Y | 0.115 | 151.1628 | 302.3256 | 906.9767 | 120 | 89.7674 | 55 | 0.001767 | 0.819 | -151.1628 | 1.7392 | 320.58 | 59.58 | 36 | 225 | 0.75562
1 | 4 | 1 | 4 | 2 | 228.7079 | 114.354 | 1.4142 | 161.7209 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | Y | 0.099 | 109.0604 | 436.2416 | 436.2416 | 120 | 98.1879 | 55 | 0.001178 | 0.819 | -109.0604 | 1.1847 | 181.86 | 19.86 | 12 | 150 | 0.79516
1 | 4 | 2 | 2 | 1 | 303.0792 | 151.5396 | 1.4142 | 214.3093 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 10 | Y | 0.115 | 151.1628 | 302.3256 | 604.6512 | 120 | 89.7674 | 55 | 0.001178 | 0.819 | -151.1628 | 1.383 | 213.72 | 39.72 | 24 | 150 | 0.70516
3 | 6 | 1 | 6 | 3 | 315.2817 | 105.0939 | 1.7321 | 182.028 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 10 | Y | 0.099 | 95.729 | 574.3741 | 574.3741 | 120 | 111.863 | 55 | 0.00096 | 0.81 | -95.729 | 1.0237 | 436.86 | 19.86 | 12 | 405 | 1.3856
3 | 6 | 3 | 2 | 1 | 614.8883 | 204.9628 | 1.7321 | 355.006 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 10 | Y | 0.115 | 206.3492 | 412.6984 | 1238.0952 | 120 | 102.4603 | 55 | 0.00096 | 0.81 | -206.3492 | 1.4485 | 500.58 | 59.58 | 36 | 405 | 0.8141
3 | 6 | 1 | 6 | 3 | 376.8361 | 125.612 | 1.7321 | 217.5664 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 10 | Y | 0.099 | 97.0149 | 582.0896 | 582.0896 | 120 | 112.6269 | 55 | 0.000552 | 0.703 | -97.0149 | 0.70842 | 1006.86 | 19.86 | 12 | 975 | 2.6719
3 | 6 | 3 | 2 | 1 | 756.6362 | 252.2121 | 1.7321 | 436.8441 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 10 | Y | 0.115 | 212.4183 | 424.8366 | 1274.5098 | 120 | 103.8562 | 55 | 0.000552 | 0.703 | -212.4183 | 0.96323 | 1070.58 | 59.58 | 36 | 975 | 1.4149
3 | 6 | 1 | 6 | 6 | 423.5931 | 141.1977 | 1.7321 | 244.5616 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | Y | 0.099 | 103.6683 | 622.0096 | 622.0096 | 120 | 116.5789 | 55 | 0.000306 | 0.691 | -103.6683 | 0.60437 | 1171.86 | 19.86 | 12 | 1140 | 2.7665
3 | 6 | 2 | 3 | 3 | 768.0697 | 256.0232 | 1.7321 | 443.4452 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | Y | 0.099 | 196.9697 | 590.9091 | 1181.8182 | 120 | 113.5 | 55 | 0.000306 | 0.691 | -196.9697 | 0.71857 | 1203.72 | 39.72 | 24 | 1140 | 1.5672
3 | 6 | 3 | 2 | 2 | 1056.7898 | 352.2633 | 1.7321 | 610.1379 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | Y | 0.099 | 281.3853 | 562.7706 | 1688.3117 | 120 | 110.7143 | 55 | 0.000306 | 0.691 | -281.3853 | 0.8219 | 1235.58 | 59.58 | 36 | 1140 | 1.1692
3 | 6 | 6 | 1 | 1 | 1551.4519 | 517.1506 | 1.7321 | 895.7312 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 10 | Y | 0.115 | 439.1892 | 439.1892 | 2635.1351 | 120 | 105.5068 | 55 | 0.000306 | 0.691 | -439.1892 | 1.015 | 1331.16 | 119.16 | 72 | 1140 | 0.85801
3 | 6 | 1 | 6 | 1 | 42.4114 | 14.1371 | 1.7321 | 24.4862 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 13 | Y | 0.11 | 27.5424 | 165.2542 | 165.2542 | 120 | 73.178 | 55 | 0.06 | 1.1 | -27.5424 | 7.8202 | 59.05 | 24.55 | 12 | 22.5 | 1.3923
1 | 4 | 1 | 4 | 1 | 34.0925 | 17.0462 | 1.4142 | 24.107 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 13 | Y | 0.11 | 30.3738 | 121.4953 | 121.4953 | 120 | 68.3645 | 55 | 0.04 | 1.1 | -30.3738 | 6.0698 | 59.05 | 24.55 | 12 | 22.5 | 1.7321
3 | 6 | 1 | 6 | 1 | 63.9468 | 21.3156 | 1.7321 | 36.9197 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 13 | Y | 0.11 | 34.9462 | 209.6774 | 209.6774 | 120 | 78.0645 | 55 | 0.03 | 1 | -34.9462 | 5.1935 | 65.35 | 24.55 | 12 | 28.8 | 1.0219
1 | 4 | 1 | 4 | 1 | 52.1118 | 26.0559 | 1.4142 | 36.8486 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 13 | Y | 0.11 | 39.6341 | 158.5366 | 158.5366 | 120 | 72.439 | 55 | 0.02 | 1 | -39.6341 | 4.1707 | 65.35 | 24.55 | 12 | 28.8 | 1.254
1 | 4 | 1 | 4 | 1 | 106.8882 | 53.4441 | 1.4142 | 75.5814 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 13 | Y | 0.11 | 77.381 | 309.5238 | 309.5238 | 120 | 89.0476 | 55 | 0.011 | 0.86 | -77.381 | 4.1444 | 60.49 | 24.55 | 12 | 23.94 | 0.56592
3 | 6 | 1 | 6 | 1 | 120.7153 | 40.2384 | 1.7321 | 69.695 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 13 | Y | 0.11 | 61.3208 | 367.9245 | 367.9245 | 120 | 95.4717 | 55 | 0.0165 | 0.86 | -61.3208 | 4.7868 | 67.42 | 24.55 | 12 | 30.87 | 0.5585
3 | 6 | 1 | 6 | 3 | 161.9242 | 53.9747 | 1.7321 | 93.487 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | Y | 0.084 | 66.0569 | 396.3415 | 396.3415 | 120 | 88.2927 | 55 | 0.006 | 0.9 | -66.0569 | 2.3954 | 75.55 | 24.55 | 12 | 39 | 0.46658
3 | 6 | 3 | 2 | 1 | 210.7875 | 70.2625 | 1.7321 | 121.6982 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | Y | 0.11 | 92.8571 | 185.7143 | 557.1429 | 120 | 75.4286 | 55 | 0.006 | 0.9 | -92.8571 | 3.0386 | 148.65 | 73.65 | 36 | 39 | 0.70521
1 | 4 | 1 | 4 | 2 | 135.9458 | 67.9729 | 1.4142 | 96.1282 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | Y | 0.084 | 79.6569 | 318.6275 | 318.6275 | 120 | 81.7647 | 55 | 0.004 | 0.9 | -79.6569 | 2.0845 | 62.55 | 24.55 | 12 | 26 | 0.46011
1 | 4 | 2 | 2 | 1 | 153.7904 | 76.8952 | 1.4142 | 108.7462 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | Y | 0.11 | 92.8571 | 185.7143 | 371.4286 | 120 | 75.4286 | 55 | 0.004 | 0.9 | -92.8571 | 2.2957 | 99.1 | 49.1 | 24 | 26 | 0.64438
3 | 6 | 1 | 6 | 3 | 214.9 | 71.6333 | 1.7321 | 124.0726 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | Y | 0.084 | 83.9793 | 503.876 | 503.876 | 120 | 97.3256 | 55 | 0.0045 | 0.85 | -83.9793 | 2.2341 | 144.55 | 24.55 | 12 | 108 | 0.67264
3 | 6 | 3 | 2 | 1 | 304.5305 | 101.5102 | 1.7321 | 175.8208 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | Y | 0.11 | 132.6531 | 265.3061 | 795.9184 | 120 | 84.1837 | 55 | 0.0045 | 0.85 | -132.6531 | 3.1103 | 217.65 | 73.65 | 36 | 108 | 0.71471
1 | 4 | 1 | 4 | 2 | 189.2046 | 94.6023 | 1.4142 | 133.7878 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | Y | 0.084 | 107.2607 | 429.0429 | 429.0429 | 120 | 91.0396 | 55 | 0.003 | 0.85 | -107.2607 | 2.0096 | 108.55 | 24.55 | 12 | 72 | 0.57372
1 | 4 | 2 | 2 | 1 | 223.7648 | 111.8824 | 1.4142 | 158.2256 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | Y | 0.11 | 132.6531 | 265.3061 | 530.6122 | 120 | 84.1837 | 55 | 0.003 | 0.85 | -132.6531 | 2.3143 | 145.1 | 49.1 | 24 | 72 | 0.64845
3 | 6 | 1 | 6 | 3 | 281.297 | 93.7657 | 1.7321 | 162.4069 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.084 | 92.3295 | 553.9773 | 553.9773 | 120 | 101.5341 | 55 | 0.001767 | 0.819 | -92.3295 | 1.3233 | 261.55 | 24.55 | 12 | 225 | 0.9298
3 | 6 | 3 | 2 | 1 | 432.4188 | 144.1396 | 1.7321 | 249.6571 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.11 | 154.7619 | 309.5238 | 928.5714 | 120 | 89.0476 | 55 | 0.001767 | 0.819 | -154.7619 | 1.7646 | 334.65 | 73.65 | 36 | 225 | 0.7739
1 | 4 | 1 | 4 | 2 | 250.875 | 125.4375 | 1.4142 | 177.3954 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.084 | 121.2687 | 485.0746 | 485.0746 | 120 | 95.7463 | 55 | 0.001178 | 0.819 | -121.2687 | 1.2422 | 186.55 | 24.55 | 12 | 150 | 0.7436
1 | 4 | 2 | 2 | 1 | 309.1813 | 154.5907 | 1.4142 | 218.6242 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.11 | 154.7619 | 309.5238 | 619.0476 | 120 | 89.0476 | 55 | 0.001178 | 0.819 | -154.7619 | 1.4 | 223.1 | 49.1 | 24 | 150 | 0.72158
3 | 6 | 1 | 6 | 3 | 358.0742 | 119.3581 | 1.7321 | 206.7342 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 13 | Y | 0.084 | 110.3565 | 662.1392 | 662.1392 | 120 | 110.6197 | 55 | 0.00096 | 0.81 | -110.3565 | 1.0799 | 441.55 | 24.55 | 12 | 405 | 1.2331
3 | 6 | 3 | 2 | 1 | 631.6777 | 210.5592 | 1.7321 | 364.6993 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 13 | Y | 0.11 | 213.1148 | 426.2295 | 1278.6885 | 120 | 101.8852 | 55 | 0.00096 | 0.81 | -213.1148 | 1.4745 | 514.65 | 73.65 | 36 | 405 | 0.81474
13
3 | 6 | 1 | 6 | 3 | 429.8784 | 143.2928 | 1.7321 | 248.1904 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 13 | Y | 0.084 | 112.069 | 672.4138 | 672.4138 | 120 | 111.4828 | 55 | 0.000552 | 0.703 | -112.069 | 0.74166 | 1011.55 | 24.55 | 12 | 975 | 2.3531
3 | 6 | 3 | 2 | 1 | 778.4826 | 259.4942 | 1.7321 | 449.4572 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 13 | Y | 0.11 | 219.5946 | 439.1892 | 1317.5676 | 120 | 103.3108 | 55 | 0.000552 | 0.703 | -219.5946 | 0.97907 | 1084.65 | 73.65 | 36 | 975 | 1.3933
3 | 6 | 1 | 6 | 6 | 490.0611 | 163.3537 | 1.7321 | 282.9369 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | Y | 0.084 | 121.0428 | 726.257 | 726.257 | 120 | 116.0056 | 55 | 0.000306 | 0.691 | -121.0428 | 0.62564 | 1176.55 | 24.55 | 12 | 1140 | 2.4008
3 | 6 | 2 | 3 | 3 | 876.7153 | 292.2384 | 1.7321 | 506.1718 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | Y | 0.084 | 228.0702 | 684.2105 | 1368.4211 | 120 | 112.4737 | 55 | 0.000306 | 0.691 | -228.0702 | 0.75664 | 1213.1 | 49.1 | 24 | 1140 | 1.3837
3 | 6 | 3 | 2 | 2 | 1193.658 | 397.886 | 1.7321 | 689.1588 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | Y | 0.084 | 323.3831 | 646.7662 | 1940.2985 | 120 | 109.3284 | 55 | 0.000306 | 0.691 | -323.3831 | 0.8733 | 1249.65 | 73.65 | 36 | 1140 | 1.0469
3 | 6 | 6 | 1 | 1 | 1596.9682 | 532.3227 | 1.7321 | 922.01 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 13 | Y | 0.11 | 454.5455 | 454.5455 | 2727.2727 | 120 | 105 | 55 | 0.000306 | 0.691 | -454.5455 | 1.0338 | 1359.3 | 147.3 | 72 | 1140 | 0.85118
3 | 6 | 1 | 6 | 1 | 42.7143 | 14.2381 | 1.7321 | 24.6611 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 15 | Y | 0.106 | 27.8253 | 166.9521 | 166.9521 | 120 | 72.6969 | 55 | 0.06 | 1.1 | -27.8253 | 7.8881 | 62.76 | 28.26 | 12 | 22.5 | 1.4693
1 | 4 | 1 | 4 | 1 | 34.2779 | 17.139 | 1.4142 | 24.2382 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 15 | Y | 0.106 | 30.6026 | 122.4105 | 122.4105 | 120 | 67.9755 | 55 | 0.04 | 1.1 | -30.6026 | 6.1064 | 62.76 | 28.26 | 12 | 22.5 | 1.8309
3 | 6 | 1 | 6 | 1 | 64.5466 | 21.5155 | 1.7321 | 37.266 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 15 | Y | 0.106 | 35.4031 | 212.4183 | 212.4183 | 120 | 77.5163 | 55 | 0.03 | 1 | -35.4031 | 5.2484 | 69.06 | 28.26 | 12 | 28.8 | 1.0699
1 | 4 | 1 | 4 | 1 | 52.4935 | 26.2468 | 1.4142 | 37.1185 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 15 | Y | 0.106 | 40.0246 | 160.0985 | 160.0985 | 120 | 71.9704 | 55 | 0.02 | 1 | -40.0246 | 4.202 | 69.06 | 28.26 | 12 | 28.8 | 1.3156
1 | 4 | 1 | 4 | 1 | 108.3585 | 54.1793 | 1.4142 | 76.6211 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 15 | Y | 0.106 | 78.8835 | 315.534 | 315.534 | 120 | 88.4466 | 55 | 0.011 | 0.86 | -78.8835 | 4.2105 | 64.2 | 28.26 | 12 | 23.94 | 0.59248
3 | 6 | 1 | 6 | 1 | 122.6538 | 40.8846 | 1.7321 | 70.8142 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 15 | Y | 0.106 | 62.7413 | 376.4479 | 376.4479 | 120 | 94.9035 | 55 | 0.0165 | 0.86 | -62.7413 | 4.8805 | 71.13 | 28.26 | 12 | 30.87 | 0.57993
3 | 6 | 1 | 6 | 3 | 171.9041 | 57.3014 | 1.7321 | 99.2489 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 71.2719 | 427.6316 | 427.6316 | 120 | 85.7895 | 55 | 0.006 | 0.9 | -71.2719 | 2.5205 | 79.26 | 28.26 | 12 | 39 | 0.46107
3 | 6 | 3 | 2 | 1 | 212.6311 | 70.877 | 1.7321 | 122.7626 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 93.9306 | 187.8613 | 563.5838 | 120 | 74.9133 | 55 | 0.006 | 0.9 | -93.9306 | 3.0643 | 159.78 | 84.78 | 36 | 39 | 0.75144
1 | 4 | 1 | 4 | 2 | 142.7777 | 71.3888 | 1.4142 | 100.9591 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 84.6354 | 338.5417 | 338.5417 | 120 | 79.375 | 55 | 0.004 | 0.9 | -84.6354 | 2.1642 | 66.26 | 28.26 | 12 | 26 | 0.46408
1 | 4 | 2 | 2 | 1 | 155.2047 | 77.6024 | 1.4142 | 109.7463 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 93.9306 | 187.8613 | 375.7225 | 120 | 74.9133 | 55 | 0.004 | 0.9 | -93.9306 | 2.3129 | 106.52 | 56.52 | 24 | 26 | 0.68632
3 | 6 | 1 | 6 | 3 | 231.8976 | 77.2992 | 1.7321 | 133.8862 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.072 | 92.5926 | 555.5556 | 555.5556 | 120 | 95 | 55 | 0.0045 | 0.85 | -92.5926 | 2.3892 | 148.26 | 28.26 | 12 | 108 | 0.63933
3 | 6 | 3 | 2 | 1 | 308.2639 | 102.7546 | 1.7321 | 177.9763 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.106 | 134.8548 | 269.7095 | 809.1286 | 120 | 83.5892 | 55 | 0.0045 | 0.85 | -134.8548 | 3.1499 | 228.78 | 84.78 | 36 | 108 | 0.74216
1 | 4 | 1 | 4 | 2 | 202.0473 | 101.0237 | 1.4142 | 142.869 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.072 | 116.4875 | 465.9498 | 465.9498 | 120 | 88.5484 | 55 | 0.003 | 0.85 | -116.4875 | 2.1203 | 112.26 | 28.26 | 12 | 72 | 0.55561
1 | 4 | 2 | 2 | 1 | 226.6511 | 113.3256 | 1.4142 | 160.2665 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.106 | 134.8548 | 269.7095 | 539.4191 | 120 | 83.5892 | 55 | 0.003 | 0.85 | -134.8548 | 2.3408 | 152.52 | 56.52 | 24 | 72 | 0.67293
3 | 6 | 1 | 6 | 3 | 308.3531 | 102.7844 | 1.7321 | 178.0278 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.072 | 102.8481 | 617.0886 | 617.0886 | 120 | 99.4304 | 55 | 0.001767 | 0.819 | -102.8481 | 1.3977 | 265.26 | 28.26 | 12 | 225 | 0.86025
3 | 6 | 3 | 2 | 1 | 439.1851 | 146.395 | 1.7321 | 253.5636 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 946.6019 | 120 | 88.4466 | 55 | 0.001767 | 0.819 | -157.767 | 1.7859 | 345.78 | 84.78 | 36 | 225 | 0.78732
1 | 4 | 1 | 4 | 2 | 272.0429 | 136.0214 | 1.4142 | 192.3634 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.072 | 133.1967 | 532.7869 | 532.7869 | 120 | 93.3607 | 55 | 0.001178 | 0.819 | -133.1967 | 1.2984 | 190.26 | 28.26 | 12 | 150 | 0.69938
1 | 4 | 2 | 2 | 1 | 314.248 | 157.124 | 1.4142 | 222.2069 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 631.068 | 120 | 88.4466 | 55 | 0.001178 | 0.819 | -157.767 | 1.4142 | 230.52 | 56.52 | 24 | 150 | 0.73356
3 | 6 | 1 | 6 | 3 | 401.8526 | 133.9509 | 1.7321 | 232.0097 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.072 | 125.7253 | 754.352 | 754.352 | 120 | 109.3133 | 55 | 0.00096 | 0.81 | -125.7253 | 1.1389 | 445.26 | 28.26 | 12 | 405 | 1.108
3 | 6 | 3 | 2 | 1 | 645.8075 | 215.2692 | 1.7321 | 372.8572 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.106 | 218.8552 | 437.7104 | 1313.1313 | 120 | 101.3973 | 55 | 0.00096 | 0.81 | -218.8552 | 1.4965 | 525.78 | 84.78 | 36 | 405 | 0.81414
3 | 6 | 1 | 6 | 3 | 484.571 | 161.5237 | 1.7321 | 279.7672 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.072 | 127.9528 | 767.7165 | 767.7165 | 120 | 110.2756 | 55 | 0.000552 | 0.703 | -127.9528 | 0.77673 | 1015.26 | 28.26 | 12 | 975 | 2.0952
3 | 6 | 3 | 2 | 1 | 796.9136 | 265.6379 | 1.7321 | 460.0983 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.106 | 225.6944 | 451.3889 | 1354.1667 | 120 | 102.8472 | 55 | 0.000552 | 0.703 | -225.6944 | 0.99254 | 1095.78 | 84.78 | 36 | 975 | 1.375
3 | 6 | 1 | 6 | 6 | 560.5062 | 186.8354 | 1.7321 | 323.6084 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.072 | 139.7849 | 838.7097 | 838.7097 | 120 | 115.3871 | 55 | 0.000306 | 0.691 | -139.7849 | 0.64858 | 1180.26 | 28.26 | 12 | 1140 | 2.1057
3 | 6 | 2 | 3 | 3 | 988.961 | 329.6537 | 1.7321 | 570.9769 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.072 | 261.0442 | 783.1325 | 1566.2651 | 120 | 111.3855 | 55 | 0.000306 | 0.691 | -261.0442 | 0.797 | 1220.52 | 56.52 | 24 | 1140 | 1.2341
3 | 6 | 3 | 2 | 2 | 1332.3241 | 444.108 | 1.7321 | 769.2177 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.072 | 367.2316 | 734.4633 | 2203.3898 | 120 | 107.8814 | 55 | 0.000306 | 0.691 | -367.2316 | 0.92697 | 1260.78 | 84.78 | 36 | 1140 | 0.9463
3 | 6 | 6 | 1 | 1 | 1635.4136 | 545.1379 | 1.7321 | 944.2065 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.106 | 467.6259 | 467.6259 | 2805.7554 | 120 | 104.5683 | 55 | 0.000306 | 0.691 | -467.6259 | 1.0499 | 1381.56 | 169.56 | 72 | 1140 | 0.84478
IdcMax | as a fonction of TjMax |  |  | ASSEMBLY COST
HS250 |  | NO FAN | [25 empty] | Equation |  | Solution | Discriminant
3Φ-1Φ-BD-FWD |  |  |  |  | Includes safety factor on Tj |  |  |  |  | Device Parameters | [8 empty] | Operational Conditions | [8 empty] | ax2+bx+c=0 |  | (-b±√(D))/2a | [6 empty] | FWD | [6 empty] | BD
Circuit Type | Total number of devices = n | Number of HS | Number of devices/HS = ns | Number of Modules/HS | IdcMax | IdaveMax | F = Idrms/Idave | IdrmsMax |  | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | HS250 length | Fan | Rθsa | Pd | Pt/HS =nsxPd | Pt =nsxPd | Tj =TjMax-5 | Ts | Ta | a | b | c | D | [5 empty] | FWD AMPERAGE |  | FUSE AT 1.8x | FUSE A30QS |  |  | FWD COMPARED TO FUSE A / 10ms
[5 empty] | (A) | (A) |  | (A) |  |  | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W) | (") |  | (°C/W) | (W) | (W) | (W) | (°C) | (°C) | (°C) | F2rT | VTO | (Ta-Tj)/(Rθjc+Rθcs+nsRθsa) | D = b2-4ac | TOTAL | HS250 | FAN | MODULE | $/(A) | (A) |  | (A) | (A) | A / 10ms |  |  |  | Type | UF
3 | 6 | 1 | 6 | 1 | 42.7143 | 14.2381 | 1.7321 | 24.6611 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 15 | Y | 0.106 | 27.8253 | 166.9521 | 166.9521 | 120 | 72.6969 | 55 | 0.06 | 1.1 | -27.8253 | 7.8881 | 62.76 | 28.26 | 12 | 22.5 | 1.4693 | 17.0857 | 14.2381 | 76.8858 | 80 | 349 | 1.8729 | F1892Sxxxx |  | AC rating (V) | 300
1 | 4 | 1 | 4 | 1 | 34.2779 | 17.139 | 1.4142 | 24.2382 | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 15 | Y | 0.106 | 30.6026 | 122.4105 | 122.4105 | 120 | 67.9755 | 55 | 0.04 | 1.1 | -30.6026 | 6.1064 | 62.76 | 28.26 | 12 | 22.5 | 1.8309 | 13.7112 | 11.426 | 61.7003 | 70 | 260 | 2.0421 | F1892Sxxxx |  | DC rating (V) | 300
3 | 6 | 1 | 6 | 1 | 64.5466 | 21.5155 | 1.7321 | 37.266 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 15 | Y | 0.106 | 35.4031 | 212.4183 | 212.4183 | 120 | 77.5163 | 55 | 0.03 | 1 | -35.4031 | 5.2484 | 69.06 | 28.26 | 12 | 28.8 | 1.0699 | 25.8186 | 21.5155 | 116.1838 | 125 | 510 | 1.9366 | F1892Sxxxx
1 | 4 | 1 | 4 | 1 | 52.4935 | 26.2468 | 1.4142 | 37.1185 | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 15 | Y | 0.106 | 40.0246 | 160.0985 | 160.0985 | 120 | 71.9704 | 55 | 0.02 | 1 | -40.0246 | 4.202 | 69.06 | 28.26 | 12 | 28.8 | 1.3156 | 20.9974 | 17.4978 | 94.4884 | 100 | 461 | 1.905 | F1892Sxxxx |  | Fuse rating | A30QS
1 | 4 | 1 | 4 | 1 | 108.3585 | 54.1793 | 1.4142 | 76.6211 | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 15 | Y | 0.106 | 78.8835 | 315.534 | 315.534 | 120 | 88.4466 | 55 | 0.011 | 0.86 | -78.8835 | 4.2105 | 64.2 | 28.26 | 12 | 23.94 | 0.59248 | 43.3434 | 36.1195 | 195.0454 | 200 | 949 | 1.8457 | F1892Sxxxx |  | (A) | (A/10ms)
3 | 6 | 1 | 6 | 1 | 122.6538 | 40.8846 | 1.7321 | 70.8142 | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 15 | Y | 0.106 | 62.7413 | 376.4479 | 376.4479 | 120 | 94.9035 | 55 | 0.0165 | 0.86 | -62.7413 | 4.8805 | 71.13 | 28.26 | 12 | 30.87 | 0.57993 | 49.0615 | 40.8846 | 220.7768 | 225 | 860 | 1.8344 | F1892Sxxxx |  | 40 | 180
[45 empty] | 50 | 235
3 | 6 | 1 | 6 | 3 | 171.9041 | 57.3014 | 1.7321 | 99.2489 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 71.2719 | 427.6316 | 427.6316 | 120 | 85.7895 | 55 | 0.006 | 0.9 | -71.2719 | 2.5205 | 79.26 | 28.26 | 12 | 39 | 0.46107 | 68.7617 | F1892Dxxxx | 309.4274 | 350 | 1724 | 2.036 | F1892Sxxxx |  | 60 | 269
3 | 6 | 3 | 2 | 1 | 212.6311 | 70.877 | 1.7321 | 122.7626 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 93.9306 | 187.8613 | 563.5838 | 120 | 74.9133 | 55 | 0.006 | 0.9 | -93.9306 | 3.0643 | 159.78 | 84.78 | 36 | 39 | 0.75144 | 85.0524 | F1892Dxxxx | 382.7359 | 400 | 1984 | 1.8812 | CS61xx16B |  | 70 | 260
1 | 4 | 1 | 4 | 2 | 142.7777 | 71.3888 | 1.4142 | 100.9591 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 84.6354 | 338.5417 | 338.5417 | 120 | 79.375 | 55 | 0.004 | 0.9 | -84.6354 | 2.1642 | 66.26 | 28.26 | 12 | 26 | 0.46408 | 57.1111 | F1892Dxxxx | 256.9998 | 275 | 1196 | 1.9261 | F1892Sxxxx |  | 80 | 349
1 | 4 | 2 | 2 | 1 | 155.2047 | 77.6024 | 1.4142 | 109.7463 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 93.9306 | 187.8613 | 375.7225 | 120 | 74.9133 | 55 | 0.004 | 0.9 | -93.9306 | 2.3129 | 106.52 | 56.52 | 24 | 26 | 0.68632 | 62.0819 | F1892Dxxxx | 279.3685 | 300 | 1324 | 1.9329 | F1892Sxxxx |  | 90 | 391
[45 empty] | 100 | 461
3 | 6 | 1 | 6 | 3 | 231.8976 | 77.2992 | 1.7321 | 133.8862 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | y | 0.072 | 92.5926 | 555.5556 | 555.5556 | 120 | 95 | 55 | 0.0045 | 0.85 | -92.5926 | 2.3892 | 148.26 | 28.26 | 12 | 108 | 0.63933 | 92.7591 | F1892Dxxxx | 417.4158 | 450 | 2578 | 1.9405 | CS61xx16B |  | 125 | 510
3 | 6 | 3 | 2 | 1 | 308.2639 | 102.7546 | 1.7321 | 177.9763 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.106 | 134.8548 | 269.7095 | 809.1286 | 120 | 83.5892 | 55 | 0.0045 | 0.85 | -134.8548 | 3.1499 | 228.78 | 84.78 | 36 | 108 | 0.74216 | 123.3056 | F1892Dxxxx | 554.8751 | 600 | 3532 | 1.9464 | ND41xx35 |  | 150 | 700
1 | 4 | 1 | 4 | 2 | 202.0473 | 101.0237 | 1.4142 | 142.869 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.072 | 116.4875 | 465.9498 | 465.9498 | 120 | 88.5484 | 55 | 0.003 | 0.85 | -116.4875 | 2.1203 | 112.26 | 28.26 | 12 | 72 | 0.55561 | 80.8189 | F1892Dxxxx | 363.6852 | 400 | 1984 | 1.9797 | CS61xx16B |  | 175 | 775
1 | 4 | 2 | 2 | 1 | 226.6511 | 113.3256 | 1.4142 | 160.2665 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.106 | 134.8548 | 269.7095 | 539.4191 | 120 | 83.5892 | 55 | 0.003 | 0.85 | -134.8548 | 2.3408 | 152.52 | 56.52 | 24 | 72 | 0.67293 | 90.6604 | F1892Dxxxx | 407.972 | 450 | 2578 | 1.9854 | CS61xx16B |  | 200 | 949
[45 empty] | 225 | 860
3 | 6 | 1 | 6 | 3 | 308.3531 | 102.7844 | 1.7321 | 178.0278 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.072 | 102.8481 | 617.0886 | 617.0886 | 120 | 99.4304 | 55 | 0.001767 | 0.819 | -102.8481 | 1.3977 | 265.26 | 28.26 | 12 | 225 | 0.86025 | 123.3413 | 102.7844 | 555.0356 | 600 | 3532 | 1.9458 | ND41xx35 |  | 250 | 1058
3 | 6 | 3 | 2 | 1 | 439.1851 | 146.395 | 1.7321 | 253.5636 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 946.6019 | 120 | 88.4466 | 55 | 0.001767 | 0.819 | -157.767 | 1.7859 | 345.78 | 84.78 | 36 | 225 | 0.78732 | 175.674 | 146.395 | 790.5331 | 800 | 4196 | 1.8216 | ND41xx35 |  | 275 | 1196
1 | 4 | 1 | 4 | 2 | 272.0429 | 136.0214 | 1.4142 | 192.3634 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.072 | 133.1967 | 532.7869 | 532.7869 | 120 | 93.3607 | 55 | 0.001178 | 0.819 | -133.1967 | 1.2984 | 190.26 | 28.26 | 12 | 150 | 0.69938 | 108.8172 | 90.681 | 489.6772 | 500 | 2839 | 1.8379 | CS61xx16B |  | 300 | 1324
1 | 4 | 2 | 2 | 1 | 314.248 | 157.124 | 1.4142 | 222.2069 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 631.068 | 120 | 88.4466 | 55 | 0.001178 | 0.819 | -157.767 | 1.4142 | 230.52 | 56.52 | 24 | 150 | 0.73356 | 125.6992 | 104.7493 | 565.6465 | 600 | 3532 | 1.9093 | ND41xx35 |  | 350 | 1724
[45 empty] | 400 | 1984
3 | 6 | 1 | 6 | 3 | 401.8526 | 133.9509 | 1.7321 | 232.0097 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.072 | 125.7253 | 754.352 | 754.352 | 120 | 109.3133 | 55 | 0.00096 | 0.81 | -125.7253 | 1.1389 | 445.26 | 28.26 | 12 | 405 | 1.108 | 160.7411 | 133.9509 | 723.3348 | 800 | 4196 | 1.9908 | ND41xx35 |  | 450 | 2578
3 | 6 | 3 | 2 | 1 | 645.8075 | 215.2692 | 1.7321 | 372.8572 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.106 | 218.8552 | 437.7104 | 1313.1313 | 120 | 101.3973 | 55 | 0.00096 | 0.81 | -218.8552 | 1.4965 | 525.78 | 84.78 | 36 | 405 | 0.81414 | 258.323 | 215.2692 | 1162.4536 | 1200 | 7286 | 1.8581 | ND41xx35 |  | 500 | 2839
[45 empty] | 550 | 3110
3 | 6 | 1 | 6 | 3 | 484.571 | 161.5237 | 1.7321 | 279.7672 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.072 | 127.9528 | 767.7165 | 767.7165 | 120 | 110.2756 | 55 | 0.000552 | 0.703 | -127.9528 | 0.77673 | 1015.26 | 28.26 | 12 | 975 | 2.0952 | 193.8284 | 161.5237 | 872.2278 | 900 | 4708 | 1.8573 | ND41xx35 |  | 600 | 3532
3 | 6 | 3 | 2 | 1 | 796.9136 | 265.6379 | 1.7321 | 460.0983 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.106 | 225.6944 | 451.3889 | 1354.1667 | 120 | 102.8472 | 55 | 0.000552 | 0.703 | -225.6944 | 0.99254 | 1095.78 | 84.78 | 36 | 975 | 1.375 | 318.7654 | 265.6379 | 1434.4444 | 1500 | 10000 | 1.8823 | ND41xx35 |  | 700 | 3677
[45 empty] | 800 | 4196
3 | 6 | 1 | 6 | 6 | 560.5062 | 186.8354 | 1.7321 | 323.6084 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.072 | 139.7849 | 838.7097 | 838.7097 | 120 | 115.3871 | 55 | 0.000306 | 0.691 | -139.7849 | 0.64858 | 1180.26 | 28.26 | 12 | 1140 | 2.1057 | 224.2025 | 186.8354 | 1008.9112 | 1200 | 7286 | 2.1409 | ND41xx35 |  | 900 | 4708
3 | 6 | 2 | 3 | 3 | 988.961 | 329.6537 | 1.7321 | 570.9769 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.072 | 261.0442 | 783.1325 | 1566.2651 | 120 | 111.3855 | 55 | 0.000306 | 0.691 | -261.0442 | 0.797 | 1220.52 | 56.52 | 24 | 1140 | 1.2341 | 395.5844 | 329.6537 | 1780.1298 | 1800 | 11777 | 1.8201 | ND41xx35 |  | 1000 | 5564
3 | 6 | 3 | 2 | 2 | 1332.3241 | 444.108 | 1.7321 | 769.2177 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.072 | 367.2316 | 734.4633 | 2203.3898 | 120 | 107.8814 | 55 | 0.000306 | 0.691 | -367.2316 | 0.92697 | 1260.78 | 84.78 | 36 | 1140 | 0.9463 | 532.9297 | 444.108 | 2398.1834 | 2500 | 16826 | 1.8764 | ND41xx35 |  | 1200 | 7286
3 | 6 | 6 | 1 | 1 | 1635.4136 | 545.1379 | 1.7321 | 944.2065 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.106 | 467.6259 | 467.6259 | 2805.7554 | 120 | 104.5683 | 55 | 0.000306 | 0.691 | -467.6259 | 1.0499 | 1381.56 | 169.56 | 72 | 1140 | 0.84478 | 654.1654 | 545.1379 | 2943.7444 | 3000 | 19339 | 1.8344 | ND41xx35 |  | 1500 | 10000
[45 empty] | 1600 | 10900
[45 empty] | 1800 | 11777
[45 empty] | 2000 | 13464
[45 empty] | 2500 | 16826
BD | 1 | 1 | 1 | 1 | 107.0392 | 107.0392 | 1 | 107.0392 | S/S | CY8697 | 100 |  | 1500 | 125 | 1.2 | 0.001 | 0.3 | 0.1 | 15 | Y | 0.106 | 128.4585 | 128.4585 | 128.4585 | 120 | 68.6166 | 55 | 1e-06 | 1.2 | -128.4585 | 1.4405 | 55.26 | 28.26 | 12 | 15 | 0.51626 | [8 empty] | 3000 | 19339
BD | 1 | 1 | 1 | 1 | 100.7081 | 100.7081 | 1 | 100.7081 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 110.9215 | 110.9215 | 110.9215 | 120 | 66.7577 | 55 | 0.002 | 0.9 | -110.9215 | 1.6974 | 53.26 | 28.26 | 12 | 13 | 0.52886 | [8 empty] | 3500 | 23280
BD | 1 | 1 | 1 | 1 | 211.2841 | 211.2841 | 1 | 211.2841 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 15 | Y | 0.106 | 233.1606 | 233.1606 | 233.1606 | 145 | 79.715 | 55 | 0.0012 | 0.85 | -233.1606 | 1.8417 | 70.26 | 28.26 | 12 | 30 | 0.33254 | [8 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 379.3195 | 379.3195 | 1 | 379.3195 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 15 | Y | 0.106 | 294.1176 | 294.1176 | 294.1176 | 145 | 86.1765 | 55 | 0.00032 | 0.654 | -294.1176 | 0.80419 | 115.26 | 28.26 | 12 | 75 | 0.30386 | [8 empty] | 4500 | 29407
BD | 1 | 1 | 1 | 1 | 536.9916 | 536.9916 | 1 | 536.9916 | S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.106 | 471.2042 | 471.2042 | 471.2042 | 145 | 104.9476 | 55 | 0.000243 | 0.747 | -471.2042 | 1.016 | 132.26 | 28.26 | 12 | 92 | 0.2463 | [8 empty] | 5000 | verify data
BD | 1 | 1 | 1 | 1 | 940.7559 | 940.7559 | 1 | 940.7559 | S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 15 | Y | 0.106 | 647.482 | 647.482 | 647.482 | 145 | 123.6331 | 55 | 5.98e-05 | 0.632 | -647.482 | 0.5543 | 385.26 | 28.26 | 12 | 345 | 0.40952
BD | 1 | 1 | 1 | 1 | 83.3275 | 83.3275 | 1 | 83.3275 | S/S | CY8697 | 100 |  | 1500 | 125 | 1.2 | 0.001 | 0.3 | 0.1 | 15 | N | 0.25 | 100 | 100 | 100 | 120 | 80 | 55 | 1e-06 | 1.2 | -100 | 1.4404 | 43.26 | 28.26 | 0 | 15 | 0.51916
BD | 1 | 1 | 1 | 1 | 73.17 | 73.17 | 1 | 73.17 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | N | 0.369 | 76.5607 | 76.5607 | 76.5607 | 120 | 83.2509 | 55 | 0.002 | 0.9 | -76.5607 | 1.4225 | 29.35 | 16.35 | 0 | 13 | 0.40112
BD | 1 | 1 | 1 | 1 | 98.4373 | 98.4373 | 1 | 98.4373 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | Y | 0.122 | 107.9734 | 107.9734 | 107.9734 | 120 | 68.1728 | 55 | 0.002 | 0.9 | -107.9734 | 1.6738 | 41.35 | 16.35 | 12 | 13 | 0.42006
BD | 1 | 1 | 1 | 1 | 80.5948 | 80.5948 | 1 | 80.5948 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | N | 0.28 | 85.5263 | 85.5263 | 85.5263 | 120 | 78.9474 | 55 | 0.002 | 0.9 | -85.5263 | 1.4942 | 32.86 | 19.86 | 0 | 13 | 0.40772
BD | 1 | 1 | 1 | 1 | 99.4177 | 99.4177 | 1 | 99.4177 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.115 | 109.2437 | 109.2437 | 109.2437 | 120 | 67.563 | 55 | 0.002 | 0.9 | -109.2437 | 1.6839 | 44.86 | 19.86 | 12 | 13 | 0.45123
BD | 1 | 1 | 1 | 1 | 82.9654 | 82.9654 | 1 | 82.9654 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | N | 0.255 | 88.4354 | 88.4354 | 88.4354 | 120 | 77.551 | 55 | 0.002 | 0.9 | -88.4354 | 1.5175 | 37.55 | 24.55 | 0 | 13 | 0.4526
BD | 1 | 1 | 1 | 1 | 100.1304 | 100.1304 | 1 | 100.1304 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | Y | 0.11 | 110.1695 | 110.1695 | 110.1695 | 120 | 67.1186 | 55 | 0.002 | 0.9 | -110.1695 | 1.6914 | 49.55 | 24.55 | 12 | 13 | 0.49485
BD | 1 | 1 | 1 | 1 | 83.4567 | 83.4567 | 1 | 83.4567 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | N | 0.25 | 89.0411 | 89.0411 | 89.0411 | 120 | 77.2603 | 55 | 0.002 | 0.9 | -89.0411 | 1.5223 | 41.26 | 28.26 | 0 | 13 | 0.49439
BD | 1 | 1 | 1 | 1 | 100.7081 | 100.7081 | 1 | 100.7081 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 110.9215 | 110.9215 | 110.9215 | 120 | 66.7577 | 55 | 0.002 | 0.9 | -110.9215 | 1.6974 | 53.26 | 28.26 | 12 | 13 | 0.52886
BD | 1 | 1 | 1 | 1 | 136.7472 | 136.7472 | 1 | 136.7472 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 6.5 | N | 0.369 | 138.6749 | 138.6749 | 138.6749 | 145 | 106.171 | 55 | 0.0012 | 0.85 | -138.6749 | 1.3881 | 46.35 | 16.35 | 0 | 30 | 0.33895
BD | 1 | 1 | 1 | 1 | 204.404 | 204.404 | 1 | 204.404 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 6.5 | Y | 0.122 | 223.8806 | 223.8806 | 223.8806 | 145 | 82.3134 | 55 | 0.0012 | 0.85 | -223.8806 | 1.7971 | 58.35 | 16.35 | 12 | 30 | 0.28546
BD | 1 | 1 | 1 | 1 | 207.3558 | 207.3558 | 1 | 207.3558 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 10 | y | 0.115 | 227.8481 | 227.8481 | 227.8481 | 145 | 81.2025 | 55 | 0.0012 | 0.85 | -227.8481 | 1.8162 | 61.86 | 19.86 | 12 | 30 | 0.29833
BD | 1 | 1 | 1 | 1 | 161.2176 | 161.2176 | 1 | 161.2176 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 13 | N | 0.255 | 168.2243 | 168.2243 | 168.2243 | 145 | 97.8972 | 55 | 0.0012 | 0.85 | -168.2243 | 1.53 | 54.55 | 24.55 | 0 | 30 | 0.33836
BD | 1 | 1 | 1 | 1 | 211.2841 | 211.2841 | 1 | 211.2841 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 15 | y | 0.106 | 233.1606 | 233.1606 | 233.1606 | 145 | 79.715 | 55 | 0.0012 | 0.85 | -233.1606 | 1.8417 | 70.26 | 28.26 | 12 | 30 | 0.33254
BD | 1 | 1 | 1 | 1 | 218.4946 | 218.4946 | 1 | 218.4946 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 6.5 | N | 0.369 | 158.1722 | 158.1722 | 158.1722 | 145 | 113.3656 | 55 | 0.00032 | 0.654 | -158.1722 | 0.63018 | 91.35 | 16.35 | 0 | 75 | 0.41809
BD | 1 | 1 | 1 | 1 | 254.9045 | 254.9045 | 1 | 254.9045 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 10 | N | 0.28 | 187.5 | 187.5 | 187.5 | 145 | 107.5 | 55 | 0.00032 | 0.654 | -187.5 | 0.66772 | 94.86 | 19.86 | 0 | 75 | 0.37214
BD | 1 | 1 | 1 | 1 | 267.4506 | 267.4506 | 1 | 267.4506 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 13 | N | 0.255 | 197.8022 | 197.8022 | 197.8022 | 145 | 105.4396 | 55 | 0.00032 | 0.654 | -197.8022 | 0.6809 | 99.55 | 24.55 | 0 | 75 | 0.37222
BD | 1 | 1 | 1 | 1 | 270.1113 | 270.1113 | 1 | 270.1113 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 15 | N | 0.25 | 200 | 200 | 200 | 145 | 105 | 55 | 0.00032 | 0.654 | -200 | 0.68372 | 103.26 | 28.26 | 0 | 75 | 0.38229
BD | 1 | 1 | 1 | 1 | 325.2374 | 325.2374 | 1 | 325.2374 | S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | N | 0.25 | 268.6567 | 268.6567 | 268.6567 | 145 | 122.1642 | 55 | 0.000243 | 0.747 | -268.6567 | 0.81914 | 120.26 | 28.26 | 0 | 92 | 0.36976
BD | 1 | 1 | 1 | 1 | 481.2811 | 481.2811 | 1 | 481.2811 | S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 15 | N | 0.25 | 318.0212 | 318.0212 | 318.0212 | 145 | 134.5053 | 55 | 5.98e-05 | 0.632 | -318.0212 | 0.47549 | 373.26 | 28.26 | 0 | 345 | 0.77556
BD | 1 | 1 | 1 | 1 | 317.5096 | 317.5096 | 1 | 317.5096 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.25 | 229.682 | 229.682 | 229.682 | 120 | 112.4205 | 55 | 0.000102 | 0.691 | -229.682 | 0.57119 | 218.26 | 28.26 | 0 | 190 | 0.68741
BD | 1 | 1 | 1 | 1 | 317.5096 | 317.5096 | 1 | 317.5096 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.25 | 229.682 | 229.682 | 229.682 | 120 | 112.4205 | 55 | 0.000102 | 0.691 | -229.682 | 0.57119 | 218.26 | 28.26 | 0 | 190 | 0.68741
BD | 1 | 1 | 1 | 1 | 243.9192 | 243.9192 | 1 | 243.9192 | S |  | 250 | 393 | 5900 | 150 | 0.79 | 0.63 | 0.16 | 0.125 | 15 | Y | 0.106 | 230.179 | 230.179 | 230.179 | 145 | 79.399 | 55 | 0.00063 | 0.79 | -230.179 | 1.2042 | #N/A | 28.26 | 12 | #N/A | #N/A
BD | 1 | 1 | 1 | 1 | 223.5724 | 223.5724 | 1 | 223.5724 | S |  | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.125 | 15 | Y | 0.106 | 230.179 | 230.179 | 230.179 | 145 | 79.399 | 55 | 0.00049 | 0.92 | -230.179 | 1.2976 | #N/A | 28.26 | 12 | #N/A | #N/A
BD | 1 | 1 | 1 | 1 | 282.4985 | 282.4985 | 1 | 282.4985 | S | VSKE250-12 | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.035 | 15 | y | 0.106 | 299.0033 | 299.0033 | 299.0033 | 145 | 86.6944 | 55 | 0.00049 | 0.92 | -299.0033 | 1.4324 | 86.36 | 28.26 | 12 | 46.1 | 0.3057
BD | 1 | 1 | 1 | 1 | 303.2723 | 303.2723 | 1 | 303.2723 | S | VSKE270-12 | 270 | 424 | 7500 | 150 | 0.87 | 0.81 | 0.125 | 0.035 | 15 | Y | 0.106 | 338.3459 | 338.3459 | 338.3459 | 145 | 90.8647 | 55 | 0.00081 | 0.87 | -338.3459 | 1.8531 | 40.26 | 28.26 | 12 | 0 | 0.13275
BD | 1 | 1 | 1 | 1 | 335.7504 | 335.7504 | 1 | 335.7504 | S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 15 | Y | 0.106 | 338.3459 | 338.3459 | 338.3459 | 145 | 90.8647 | 55 | 0.00044 | 0.86 | -338.3459 | 1.3351 | 94.46 | 28.26 | 12 | 54.2 | 0.28134
BD | 1 | 1 | 1 | 1 | 379.3195 | 379.3195 | 1 | 379.3195 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 15 | y | 0.106 | 294.1176 | 294.1176 | 294.1176 | 145 | 86.1765 | 55 | 0.00032 | 0.654 | -294.1176 | 0.80419 | 115.26 | 28.26 | 12 | 75 | 0.30386
BD | 1 | 1 | 1 | 1 | 275.2239 | 275.2239 | 1 | 275.2239 | S/S | VSKE250-12 | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.035 | 10 | Y | 0.115 | 290.3226 | 290.3226 | 290.3226 | 145 | 88.3871 | 55 | 0.00049 | 0.92 | -290.3226 | 1.4154 | 77.96 | 19.86 | 12 | 46.1 | 0.28326
BD | 1 | 1 | 1 | 1 | 295.0983 | 295.0983 | 1 | 295.0983 | S/S | VSKE270-12 | 270 | 424 | 7500 | 150 | 0.87 | 0.81 | 0.125 | 0.035 | 10 | Y | 0.115 | 327.2727 | 327.2727 | 327.2727 | 145 | 92.6364 | 55 | 0.00081 | 0.87 | -327.2727 | 1.8173 | 31.86 | 19.86 | 12 | 0 | 0.10796
BD | 1 | 1 | 1 | 1 | 326.1319 | 326.1319 | 1 | 326.1319 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.115 | 327.2727 | 327.2727 | 327.2727 | 145 | 92.6364 | 55 | 0.00044 | 0.86 | -327.2727 | 1.3156 | 86.06 | 19.86 | 12 | 54.2 | 0.26388
BD | 1 | 1 | 1 | 1 | 369.9172 | 369.9172 | 1 | 369.9172 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 10 | Y | 0.115 | 285.7143 | 285.7143 | 285.7143 | 145 | 87.8571 | 55 | 0.00032 | 0.654 | -285.7143 | 0.79343 | 106.86 | 19.86 | 12 | 75 | 0.28888
BD | 1 | 1 | 1 | 1 | 99.4177 | 99.4177 | 1 | 99.4177 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.115 | 109.2437 | 109.2437 | 109.2437 | 120 | 67.563 | 55 | 0.002 | 0.9 | -109.2437 | 1.6839 | 44.86 | 19.86 | 12 | 13 | 0.45123
BD | 1 | 1 | 1 | 1 | 207.3558 | 207.3558 | 1 | 207.3558 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 10 | Y | 0.115 | 227.8481 | 227.8481 | 227.8481 | 145 | 81.2025 | 55 | 0.0012 | 0.85 | -227.8481 | 1.8162 | 61.86 | 19.86 | 12 | 30 | 0.29833
BD | 1 | 1 | 1 | 1 | 193.0686 | 193.0686 | 1 | 193.0686 | S/S | VSKE166/12pbf | 165 | 260 | 3350 | 150 | 0.88 | 1.26 | 0.2 | 0.1 | 10 | Y | 0.115 | 216.8675 | 216.8675 | 216.8675 | 145 | 79.9398 | 55 | 0.00126 | 0.88 | -216.8675 | 1.8674 | 57.56 | 19.86 | 12 | 25.7 | 0.29813
BD | 1 | 1 | 1 | 1 | 275.2239 | 275.2239 | 1 | 275.2239 | S/S | VSKE250-12 | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.035 | 10 | Y | 0.115 | 290.3226 | 290.3226 | 290.3226 | 145 | 88.3871 | 55 | 0.00049 | 0.92 | -290.3226 | 1.4154 | 77.96 | 19.86 | 12 | 46.1 | 0.28326
BD | 1 | 1 | 1 | 1 | 295.0983 | 295.0983 | 1 | 295.0983 | S/S | VSKE270-12 | 270 | 424 | 7500 | 150 | 0.87 | 0.81 | 0.125 | 0.035 | 10 | Y | 0.115 | 327.2727 | 327.2727 | 327.2727 | 145 | 92.6364 | 55 | 0.00081 | 0.87 | -327.2727 | 1.8173 | 31.86 | 19.86 | 12 | 0 | 0.10796
BD | 1 | 1 | 1 | 1 | 326.1319 | 326.1319 | 1 | 326.1319 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.115 | 327.2727 | 327.2727 | 327.2727 | 145 | 92.6364 | 55 | 0.00044 | 0.86 | -327.2727 | 1.3156 | 86.06 | 19.86 | 12 | 54.2 | 0.26388
BD | 1 | 1 | 1 | 1 | 365.9413 | 365.9413 | 1 | 365.9413 | S/S | SKKE320/12 | 320 | 600 | 10000 | 150 | 0.8 | 0.35 | 0.11 | 0.04 | 10 | Y | 0.115 | 339.6226 | 339.6226 | 339.6226 | 145 | 94.0566 | 55 | 0.00035 | 0.8 | -339.6226 | 1.1155 | 31.86 | 19.86 | 12 | 0 | 0.087063
BD | 1 | 1 | 1 | 1 | 369.9172 | 369.9172 | 1 | 369.9172 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 10 | Y | 0.115 | 285.7143 | 285.7143 | 285.7143 | 145 | 87.8571 | 55 | 0.00032 | 0.654 | -285.7143 | 0.79343 | 106.86 | 19.86 | 12 | 75 | 0.28888
BD | 1 | 1 | 1 | 1 | 536.9916 | 536.9916 | 1 | 536.9916 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.106 | 471.2042 | 471.2042 | 471.2042 | 145 | 104.9476 | 55 | 0.000243 | 0.747 | -471.2042 | 1.016 | 132.26 | 28.26 | 12 | 92 | 0.2463
BD | 1 | 1 | 1 | 1 | 887.644 | 887.644 | 1 | 887.644 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.115 | 608.1081 | 608.1081 | 608.1081 | 145 | 124.9324 | 55 | 5.98e-05 | 0.632 | -608.1081 | 0.54488 | 376.86 | 19.86 | 12 | 345 | 0.42456
[10 empty] | CY8697 | 100 |  | 1500 | 125 | 1.2 |  | 0.3 | 0.1
[10 empty] | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2
[10 empty] | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1
[10 empty] | VSKE166/12pbf | 165 | 260 | 3350 | 150 | 0.88 | 1.26 | 0.2 | 0.1
[10 empty] | VSKE250-12 | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.035
[10 empty] | VSKE270-12 | 270 | 424 | 7500 | 150 | 0.87 | 0.81 | 0.125 | 0.035
[10 empty] | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035
[10 empty] | SKKE320/12 | 320 | 600 | 10000 | 150 | 0.8 | 0.35 | 0.11 | 0.04
[10 empty] | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06
[10 empty] | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02
[10 empty] | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009
BD | 1 | 1 | 1 | 1 | 395.6126 | 395.6126 | 1 | 395.6126 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.06 | 409.0909 | 409.0909 | 409.0909 | 145 | 79.5455 | 55 | 0.00044 | 0.86 | -409.0909 | 1.4596 | 86.06 | 19.86 | 12 | 54.2 | 0.21754
BD | 1 | 1 | 1 | 1 | 447.9327 | 447.9327 | 1 | 447.9327 | S/S | SKKE320/12 | 320 | 600 | 10000 | 150 | 0.8 | 0.35 | 0.11 | 0.04 | 10 | Y | 0.06 | 428.5714 | 428.5714 | 428.5714 | 145 | 80.7143 | 55 | 0.00035 | 0.8 | -428.5714 | 1.24 | 31.86 | 19.86 | 12 | 0 | 0.071127
BD | 1 | 1 | 1 | 1 | 436.192 | 436.192 | 1 | 436.192 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 10 | Y | 0.06 | 346.1538 | 346.1538 | 346.1538 | 145 | 75.7692 | 55 | 0.00032 | 0.654 | -346.1538 | 0.87079 | 106.86 | 19.86 | 12 | 75 | 0.24498
BD | 1 | 1 | 1 | 1 | 680.3401 | 680.3401 | 1 | 680.3401 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.06 | 620.6897 | 620.6897 | 620.6897 | 145 | 92.2414 | 55 | 0.000243 | 0.747 | -620.6897 | 1.1613 | 132.26 | 28.26 | 12 | 92 | 0.1944
BD | 1 | 1 | 1 | 1 | 1356.9991 | 1356.9991 | 1 | 1356.9991 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.06 | 967.7419 | 967.7419 | 967.7419 | 145 | 113.0645 | 55 | 5.98e-05 | 0.632 | -967.7419 | 0.63091 | 376.86 | 19.86 | 12 | 345 | 0.27772
BD | 1 | 1 | 1 | 1 | 395.6126 | 395.6126 | 1 | 395.6126 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.06 | 409.0909 | 409.0909 | 409.0909 | 145 | 79.5455 | 55 | 0.00044 | 0.86 | -409.0909 | 1.4596 | 86.06 | 19.86 | 12 | 54.2 | 0.21754
BD | 1 | 1 | 1 | 1 | 411.6434 | 411.6434 | 1 | 411.6434 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.05 | 428.5714 | 428.5714 | 428.5714 | 145 | 76.4286 | 55 | 0.00044 | 0.86 | -428.5714 | 1.4939 | 86.06 | 19.86 | 12 | 54.2 | 0.20906
BD | 1 | 1 | 1 | 1 | 429.0662 | 429.0662 | 1 | 429.0662 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.04 | 450 | 450 | 450 | 145 | 73 | 55 | 0.00044 | 0.86 | -450 | 1.5316 | 86.06 | 19.86 | 12 | 54.2 | 0.20058
BD | 1 | 1 | 1 | 1 | 448.0753 | 448.0753 | 1 | 448.0753 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.03 | 473.6842 | 473.6842 | 473.6842 | 145 | 69.2105 | 55 | 0.00044 | 0.86 | -473.6842 | 1.5733 | 86.06 | 19.86 | 12 | 54.2 | 0.19207
BD | 1 | 1 | 1 | 1 | 468.9035 | 468.9035 | 1 | 468.9035 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.02 | 500 | 500 | 500 | 145 | 65 | 55 | 0.00044 | 0.86 | -500 | 1.6196 | 86.06 | 19.86 | 12 | 54.2 | 0.18353
BD | 1 | 1 | 1 | 1 | 680.3401 | 680.3401 | 1 | 680.3401 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.06 | 620.6897 | 620.6897 | 620.6897 | 145 | 92.2414 | 55 | 0.000243 | 0.747 | -620.6897 | 1.1613 | 132.26 | 28.26 | 12 | 92 | 0.1944
BD | 1 | 1 | 1 | 1 | 722.6017 | 722.6017 | 1 | 722.6017 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.05 | 666.6667 | 666.6667 | 666.6667 | 145 | 88.3333 | 55 | 0.000243 | 0.747 | -666.6667 | 1.206 | 132.26 | 28.26 | 12 | 92 | 0.18303
BD | 1 | 1 | 1 | 1 | 770.6557 | 770.6557 | 1 | 770.6557 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.04 | 720 | 720 | 720 | 145 | 83.8 | 55 | 0.000243 | 0.747 | -720 | 1.2578 | 132.26 | 28.26 | 12 | 92 | 0.17162
BD | 1 | 1 | 1 | 1 | 825.8203 | 825.8203 | 1 | 825.8203 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.03 | 782.6087 | 782.6087 | 782.6087 | 145 | 78.4783 | 55 | 0.000243 | 0.747 | -782.6087 | 1.3187 | 132.26 | 28.26 | 12 | 92 | 0.16016
BD | 1 | 1 | 1 | 1 | 889.858 | 889.858 | 1 | 889.858 | S/S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.02 | 857.1429 | 857.1429 | 857.1429 | 145 | 72.1429 | 55 | 0.000243 | 0.747 | -857.1429 | 1.3912 | 132.26 | 28.26 | 12 | 92 | 0.14863
BD | 1 | 1 | 1 | 1 | 1356.9991 | 1356.9991 | 1 | 1356.9991 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.06 | 967.7419 | 967.7419 | 967.7419 | 145 | 113.0645 | 55 | 5.98e-05 | 0.632 | -967.7419 | 0.63091 | 376.86 | 19.86 | 12 | 345 | 0.27772
BD | 1 | 1 | 1 | 1 | 1502.2024 | 1502.2024 | 1 | 1502.2024 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.05 | 1084.3373 | 1084.3373 | 1084.3373 | 145 | 109.2169 | 55 | 5.98e-05 | 0.632 | -1084.3373 | 0.6588 | 376.86 | 19.86 | 12 | 345 | 0.25087
BD | 1 | 1 | 1 | 1 | 1682.8054 | 1682.8054 | 1 | 1682.8054 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.04 | 1232.8767 | 1232.8767 | 1232.8767 | 145 | 104.3151 | 55 | 5.98e-05 | 0.632 | -1232.8767 | 0.69433 | 376.86 | 19.86 | 12 | 345 | 0.22395
BD | 1 | 1 | 1 | 1 | 1913.8285 | 1913.8285 | 1 | 1913.8285 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.03 | 1428.5714 | 1428.5714 | 1428.5714 | 145 | 97.8571 | 55 | 5.98e-05 | 0.632 | -1428.5714 | 0.74114 | 376.86 | 19.86 | 12 | 345 | 0.19691
BD | 1 | 1 | 1 | 1 | 2220.3954 | 2220.3954 | 1 | 2220.3954 | S/S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 10 | Y | 0.02 | 1698.1132 | 1698.1132 | 1698.1132 | 145 | 88.9623 | 55 | 5.98e-05 | 0.632 | -1698.1132 | 0.80561 | 376.86 | 19.86 | 12 | 345 | 0.16973
3 | 6 | 1 | 6 | 3 | 555.4476 | 185.1492 | 1.7321 | 320.6878 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.06 | 149.0826 | 894.4954 | 894.4954 | 120 | 108.6697 | 55 | 0.000552 | 0.703 | -149.0826 | 0.82338 | 1015.26 | 28.26 | 12 | 975 | 1.8278 | 222.179 | 185.1492 | 999.8057 | 900 | 4708 | 1.6203 | ND41xx35 |  | 600 | 3532
3 | 6 | 3 | 2 | 1 | 1199.471 | 399.8237 | 1.7321 | 692.5149 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.05 | 369.3182 | 738.6364 | 2215.9091 | 120 | 91.9318 | 55 | 0.000552 | 0.703 | -369.3182 | 1.3097 | 1095.78 | 84.78 | 36 | 975 | 0.91355 | 479.7884 | 399.8237 | 2159.0478 | 1500 | 10000 | 1.2506 | ND41xx35 |  | 700 | 3677
3 | 6 | 1 | 6 | 3 | 736.0088 | 245.3363 | 1.7321 | 424.9349 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.04 | 205.6962 | 1234.1772 | 1234.1772 | 120 | 104.3671 | 55 | 0.000552 | 0.703 | -205.6962 | 0.94839 | 1015.26 | 28.26 | 12 | 975 | 1.3794 | 294.4035 | 245.3363 | 1324.8158 | 900 | 4708 | 1.2228 | ND41xx35 |  | 600 | 3532
3 | 6 | 3 | 2 | 1 | 1472.2565 | 490.7522 | 1.7321 | 850.0077 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.03 | 477.9412 | 955.8824 | 2867.6471 | 120 | 83.6765 | 55 | 0.000552 | 0.703 | -477.9412 | 1.5495 | 1095.78 | 84.78 | 36 | 975 | 0.74429 | 588.9026 | 490.7522 | 2650.0617 | 1500 | 10000 | 1.0188 | ND41xx35 |  | 700 | 3677
3 | 6 | 3 | 2 | 1 | 1665.3421 | 555.114 | 1.7321 | 961.4857 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.02 | 560.3448 | 1120.6897 | 3362.069 | 120 | 77.4138 | 55 | 0.000552 | 0.703 | -560.3448 | 1.7315 | 1095.78 | 84.78 | 36 | 975 | 0.65799 | 666.1368 | 555.114 | 2997.6157 | 1500 | 10000 | 0.90072 | ND41xx35 |  | 700 | 3677
3 | 6 | 1 | 6 | 6 | 654.7789 | 218.2596 | 1.7321 | 378.0368 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.06 | 165.3944 | 992.3664 | 992.3664 | 120 | 114.542 | 55 | 0.000306 | 0.691 | -165.3944 | 0.67992 | 1180.26 | 28.26 | 12 | 1140 | 1.8025 | 261.9115 | 218.2596 | 1178.602 | 1200 | 7286 | 1.8327 | ND41xx35 |  | 900 | 4708
3 | 6 | 2 | 3 | 3 | 1294.6568 | 431.5523 | 1.7321 | 747.4705 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.05 | 355.1913 | 1065.5738 | 2131.1475 | 120 | 108.2787 | 55 | 0.000306 | 0.691 | -355.1913 | 0.91224 | 1220.52 | 56.52 | 24 | 1140 | 0.94274 | 517.8627 | 431.5523 | 2330.3823 | 1800 | 11777 | 1.3903 | ND41xx35 |  | 1000 | 5564
3 | 6 | 3 | 2 | 2 | 1941.1377 | 647.0459 | 1.7321 | 1120.7164 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.04 | 575.2212 | 1150.4425 | 3451.3274 | 120 | 101.0177 | 55 | 0.000306 | 0.691 | -575.2212 | 1.1816 | 1260.78 | 84.78 | 36 | 1140 | 0.64951 | 776.4551 | 647.0459 | 3494.0478 | 2500 | 16826 | 1.2879 | ND41xx35 |  | 1200 | 7286
3 | 6 | 6 | 1 | 1 | 3079.5037 | 1026.5012 | 1.7321 | 1777.9523 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.03 | 1031.746 | 1031.746 | 6190.4762 | 120 | 85.9524 | 55 | 0.000306 | 0.691 | -1031.746 | 1.7403 | 1381.56 | 169.56 | 72 | 1140 | 0.44863 | 1231.8015 | 1026.5012 | 5543.1067 | 3000 | 19339 | 0.97418 | ND41xx35 |  | 1500 | 10000
3 | 6 | 7 | 0.85714 | -1 | 3904.046 | 1301.3487 | 1.7321 | 2254.002 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.015 | 1417.4455 | 1214.9533 | 8504.6729 | 120 | 73.2243 | 55 | 0.000306 | 0.691 | -1417.4455 | 2.2124 | -1048.18 | 197.82 | 84 | -1330 | -0.26849 | 1561.6184 | 1301.3487 | 7027.2828 | 3650 | 23280 | 0.93493 | ND41xx35 |  | 1650 | 11289

## SCR-Diode DATA
SCR Table |  |  | Device Parameters | [8 empty] | Unit Price may 2009 | EQUIVALENT DEVICES
Configuration | Manufact |  | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs |  | PRX | Semikron | International Rectifier | Vishay
|  |  | Part No | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W)
3Φ SCR/Diode Bridge | SEMIKRON | 3S/3D | SK 40 DHxx | 42 |  | 280 | 125 | 1.1 | 20 | 1.6 | 0.1 | 22.5
3Φ SCR Bridge | SEMIKRON | 3S/3S | SK70 DTxx | 68 |  | 380 | 125 | 1 | 10 | 1.1 | 0.1 | 28.8
1Φ SCR/Diode Bridge+FWD | Crydom | 2S/2D | EFG01FF | 125 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 23.94
3Φ SCR Bridge+FWD | Crydom | 3S/3S | EFG16FF | 170 |  | 1950 | 125 | 0.86 | 5.5 | 0.3 | 0.1 | 30.87
Dual SCR | Crydom | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | CD43xx90B
SCR/Diode | Crydom | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | CD42xx90B
Dual SCR | PRX | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 36
Dual SCR | Vishay | S/S | VSKT162/xxPbF | 160 | 355 | 4100 | 125 | 0.98 | 1.38 | 0.16 | 0.1 | 31.8
SCR/Diode | PRX | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 36
SCR/Diode | Vishay | S/D | VSKH162/xxPbF | 160 | 355 | 4100 | 125 | 0.98 | 1.38 | 0.16 | 0.1 | 40.3
Dual SCR | PRX | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 75
SCR/Diode | PRX | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 75
Dual SCR | PRX | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 135
SCR/Diode | PRX | S/D | LD42xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 135
Dual SCR | PRX | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 325
SCR/Diode | PRX | S/D | PD42xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 325
Single SCR | PRX | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 190
DIODE Table |  |  | Device Parameters
Configuration | Manufact |  | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs
|  |  | Part No | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W)
Single Diode | Crydom | D | CY8697 | 100 |  | 1500 | 125 | 1.2 |  | 0.3 | 0.1 | 15
Single Diode | Crydom | D | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13
Single Diode | PRX | D | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 30
Single Diode | Vishay | D | VSKE166/12pbf | 165 | 260 | 3350 | 150 | 0.88 | 1.26 | 0.2 | 0.1 | 25.7
Single Diode | Vishay | D | VSKE250-12 | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.035 | 46.1
Single Diode | Vishay | D | VSKE270-12 | 270 | 424 | 7500 | 150 | 0.87 | 0.81 | 0.125 | 0.035
Single Diode | Vishay | D | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 54.2
Single Diode | Semikron | D | SKKE320/12 | 320 | 600 | 10000 | 150 | 0.8 | 0.35 | 0.11 | 0.04
Dual Diode | PRX | DD | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 75
Single Diode | PRX | D | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 92
Single Diode | PRX | D | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 345

## SCR Mechanical
PRX | Semikron | IXYS | Crydom |  | Torque |  |  | Torque
[5 empty] | Mech. Mounting |  |  | Electrical connection
|  |  |  | Fig. | (Nm) | (Ft-lbs) | Inch-lbs | (Nm) | (Ft-lbs) | Inch-lbs
Part No | Part No | Part No | Part No |  | ±15% | ±15% | ±15% | ±15% | ±15% | ±15%
| SK 40 Dx..SK 70 Dx |  |  | 1 | 2.5 | 1.844 | 22.128 | N/A | N/A | N/A
| SKKx 27…SKKx 106 | MCC26…MCC95 | F18 | 2 | 5 | 3.688 | 44.256 | 3 | 2.2128 | 26.5536
| SKKx 122…SKKx 162 | MCC132…MCC162 |  | 3 | 5 | 3.688 | 44.256 | 5 | 3.688 | 44.256
| SKKx 213…SKKx 430 | MCC225…MCC312 |  | 4 | 5 | 3.688 | 44.256 | 9 | 6.6384 | 79.6608
| SKKx 430…SKKx 500 | MCC500 |  | 5 | 5 | 3.688 | 44.256 | 12 | 8.8512 | 106.2144
|  |  | M50 | 6 | 1.81 | 1.3351 | 16.0207 | 5.5 | 4.0568 | 48.6816
|  |  | EF | 7 | 1.81 | 1.3351 | 16.0207 | 7 | 5.1632 | 61.9584
LS41xx60 |  |  |  | 8 | 6 | 4.4256 | 53.1072 | 12 | 8.8512 | 106.2144
PS41xx25 |  |  |  | 9 | 15 | 11.064 | 132.768 | 12 | 8.8512 | 106.2144
PS43xx15 |  |  |  | 10 | 15 | 11.064 | 132.768 | 12 | 8.8512 | 106.2144
LD43xx50 |  |  |  | 11 | 6 | 4.4256 | 53.1072 | 12 | 8.8512 | 106.2144
PD43xx07 |  |  |  | 12 | 15 | 11.064 | 132.768 | 12 | 8.8512 | 106.2144
Grade 5, steel, not specially lubricated
|  |  |  | Size | (Nm) | (Ft-lbs) | (Inch-lbs)
|  |  |  | #6-32 | 1.8078 | 1.3334 | 16
|  |  |  | #6-40 | 2.0337 | 1.5001 | 18
Fig1 | Fig5 | Fig9 |  | #8-32 | 3.3895 | 2.5001 | 30
|  |  |  | #8-36 | 3.5025 | 2.5835 | 31
|  |  |  | #10-24 | 4.8583 | 3.5835 | 43
|  |  |  | #10-32 | 5.5363 | 4.0835 | 49
|  |  |  | # 1/4-20 | 10.8465 | 8.0004 | 96
|  |  |  | # 5/16-18 | 23.0489 | 17.0009 | 204
Fig2 | Fig6 | Fig10 |  | # 3/8-16 | 40.6745 | 30.0015 | 360
|  |  |  | # 7/16-14 | 67.7909 | 50.0026 | 600
|  |  |  | # 1/2-13 | 101.6863 | 75.0038 | 900
Fig3 | Fig7 | Fig11
Fig4 | Fig8
Fig12

## SCR Assemblies
SCR Assemblies final
3Φ-1Φ-BD-FWD |  |  |  |  | Includes safety factor on Tj |  |  |  |  | Device Parameters | [8 empty] | Operational Conditions | [8 empty] | ax2+bx+c=0 |  | (-b±√(D))/2a | [8 empty] | FWD | [6 empty] | BD
Circuit Type | Total number of devices = n | Number of HS | Number of devices/HS = ns | Number of Modules/HS | IdcMax | IdaveMax | F = Idrms/Idave | IdrmsMax |  | Device Part No | Idave Max | Idrms Max | Ifsm | Tj Max | VTO | rT | Per Junction Rθjc | Per Junction Rθcs | HS250 length | Fan | Rθsa | Pd | Pt/HS =nsxPd | Pt =nsxPd | Tj =TjMax-5 | Ts | Ta | a | b | c | D | [7 empty] | FWD AMPERAGE |  | FUSE AT 1.8x | FUSE A30QS |  |  | FWD COMPARED TO FUSE A / 10ms
[5 empty] | (A) | (A) |  | (A) |  |  | (A) | (A) | (A) | (°C) | (V) | (mΩ) | (°C/W) | (°C/W) | (") |  | (°C/W) | (W) | (W) | (W) | (°C) | (°C) | (°C) | F2rT | VTO | (Ta-Tj)/(Rθjc+Rθcs+nsRθsa) | D = b2-4ac | TOTAL |  | HS250 | FAN | MODULE | $/(A) |  | (A) |  | (A) | (A) | A / 10ms |  |  |  | Type | UF
3 | 6 | 1 | 6 | 3 | 171.9041 | 57.3014 | 1.7321 | 99.2489 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 71.2719 | 427.6316 | 427.6316 | 120 | 85.7895 | 55 | 0.006 | 0.9 | -71.2719 | 2.5205 | 79.26 |  | 28.26 | 12 | 39 | 0.46107 |  | 68.7617 | F1892Dxxxx | 309.4274 | 350 | 1724 | 2.036 | F1892Sxxxx |  | 60 | 269
[5 empty] | 150 | [35 empty] | 270 | 275 | 1196 | 1.8333 | F1892Sxxxx
1 | 4 | 1 | 4 | 2 | 142.7777 | 71.3888 | 1.4142 | 100.9591 | S/D | F1892HDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 84.6354 | 338.5417 | 338.5417 | 120 | 79.375 | 55 | 0.004 | 0.9 | -84.6354 | 2.1642 | 66.26 |  | 28.26 | 12 | 26 | 0.46408 |  | 57.1111 | F1892Dxxxx | 256.9998 | 275 | 1196 | 1.9261 | F1892Sxxxx |  | 80 | 349
[47 empty] | 100 | 461
3 | 6 | 1 | 6 | 3 | 231.8976 | 77.2992 | 1.7321 | 133.8862 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.072 | 92.5926 | 555.5556 | 555.5556 | 120 | 95 | 55 | 0.0045 | 0.85 | -92.5926 | 2.3892 | 148.26 |  | 28.26 | 12 | 108 | 0.63933 |  | 92.7591 | F1892Dxxxx | 417.4158 | 450 | 2578 | 1.9405 | CS61xx16B |  | 125 | 510
[5 empty] | 225 | [27 empty] | 0.65893 | [7 empty] | 405 | 450 | 2578
3 | 6 | 3 | 2 | 1 | 308.2639 | 102.7546 | 1.7321 | 177.9763 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.106 | 134.8548 | 269.7095 | 809.1286 | 120 | 83.5892 | 55 | 0.0045 | 0.85 | -134.8548 | 3.1499 | 228.78 |  | 84.78 | 36 | 108 | 0.74216 |  | 123.3056 | F1892Dxxxx | 554.8751 | 600 | 3532 | 1.9464 | ND41xx35 |  | 150 | 700
1 | 4 | 1 | 4 | 2 | 202.0473 | 101.0237 | 1.4142 | 142.869 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.072 | 116.4875 | 465.9498 | 465.9498 | 120 | 88.5484 | 55 | 0.003 | 0.85 | -116.4875 | 2.1203 | 112.26 |  | 28.26 | 12 | 72 | 0.55561 |  | 80.8189 | F1892Dxxxx | 363.6852 | 400 | 1984 | 1.9797 | CS61xx16B |  | 175 | 775
[5 empty] | 200 | [27 empty] | 0.5613
[47 empty] | 225 | 860
3 | 6 | 1 | 6 | 3 | 308.3531 | 102.7844 | 1.7321 | 178.0278 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.072 | 102.8481 | 617.0886 | 617.0886 | 120 | 99.4304 | 55 | 0.001767 | 0.819 | -102.8481 | 1.3977 | 265.26 |  | 28.26 | 12 | 225 | 0.86025 |  | 123.3413 | 102.7844 | 555.0356 | 600 | 3532 | 1.9458 | ND41xx35 |  | 250 | 1058
[5 empty] | 300 | [27 empty] | 0.8842
3 | 6 | 3 | 2 | 1 | 439.1851 | 146.395 | 1.7321 | 253.5636 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 946.6019 | 120 | 88.4466 | 55 | 0.001767 | 0.819 | -157.767 | 1.7859 | 345.78 |  | 84.78 | 36 | 225 | 0.78732 |  | 175.674 | 146.395 | 790.5331 | 800 | 4196 | 1.8216 | ND41xx35 |  | 275 | 1196
[5 empty] | 450 | [27 empty] | 0.7684
1 | 4 | 1 | 4 | 2 | 250.875 | 125.4375 | 1.4142 | 177.3954 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.084 | 121.2687 | 485.0746 | 485.0746 | 120 | 95.7463 | 55 | 0.001178 | 0.819 | -121.2687 | 1.2422 | 186.55 |  | 24.55 | 12 | 150 | 0.7436 |  | 100.35 | 83.625 | 451.5751 | 500 | 2839 | 1.993 | CS61xx16B |  | 300 | 1324
250
1 | 4 | 2 | 2 | 1 | 314.248 | 157.124 | 1.4142 | 222.2069 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 631.068 | 120 | 88.4466 | 55 | 0.001178 | 0.819 | -157.767 | 1.4142 | 230.52 |  | 56.52 | 24 | 150 | 0.73356 |  | 125.6992 | 104.7493 | 565.6465 | 600 | 3532 | 1.9093 | ND41xx35 |  | 350 | 1724
300
[47 empty] | 400 | 1984
3 | 6 | 1 | 6 | 3 | 401.8526 | 133.9509 | 1.7321 | 232.0097 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.072 | 125.7253 | 754.352 | 754.352 | 120 | 109.3133 | 55 | 0.00096 | 0.81 | -125.7253 | 1.1389 | 445.26 |  | 28.26 | 12 | 405 | 1.108 |  | 160.7411 | 133.9509 | 723.3348 | 800 | 4196 | 1.9908 | ND41xx35 |  | 450 | 2578
1 | 4 | 2 | 2 | 1 | 457.6428 | 228.8214 | 1.4142 | 323.6023 | S/S | LD42xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.106 | 218.8552 | 437.7104 | 875.4209 | 120 | 101.3973 | 55 | 0.00064 | 0.81 | -218.8552 | 1.2164 | 350.52 |  | 56.52 | 24 | 270 | 0.76592 |  | 183.0571 | 152.5476 | 823.757 | 800 | 4196 | 1.7481 | ND41xx35 |  | 450 | 2578
3 | 6 | 3 | 2 | 1 | 645.8075 | 215.2692 | 1.7321 | 372.8572 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.106 | 218.8552 | 437.7104 | 1313.1313 | 120 | 101.3973 | 55 | 0.00096 | 0.81 | -218.8552 | 1.4965 | 525.78 |  | 84.78 | 36 | 405 | 0.81414 |  | 258.323 | 215.2692 | 1162.4536 | 1200 | 7286 | 1.8581 | ND41xx35 |  | 500 | 2839
[5 empty] | 650 | [27 empty] | 0.80889
[47 empty] | 550 | 3110
3 | 6 | 3 | 2 | 1 | 796.9136 | 265.6379 | 1.7321 | 460.0983 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.106 | 225.6944 | 451.3889 | 1354.1667 | 120 | 102.8472 | 55 | 0.000552 | 0.703 | -225.6944 | 0.99254 | 1095.78 |  | 84.78 | 36 | 975 | 1.375 |  | 318.7654 | 265.6379 | 1434.4444 | 1500 | 10000 | 1.8823 | ND41xx35 |  | 700 | 3677
[5 empty] | 825 | [27 empty] | 1.3282
[47 empty] | 800 | 4196
3 | 6 | 6 | 1 | 1 | 1635.4136 | 545.1379 | 1.7321 | 944.2065 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.106 | 467.6259 | 467.6259 | 2805.7554 | 120 | 104.5683 | 55 | 0.000306 | 0.691 | -467.6259 | 1.0499 | 1381.56 |  | 169.56 | 72 | 1140 | 0.84478 |  | 654.1654 | 545.1379 | 2943.7444 | 3000 | 19339 | 1.8344 | ND41xx35 |  | 1500 | 10000
[5 empty] | 1700 | [27 empty] | 0.81268
[47 empty] | 1600 | 10900
[47 empty] | 1800 | 11777
[47 empty] | 2000 | 13464
[47 empty] | 2500 | 16826
BD | 1 | 1 | 1 | 1 | 107.0392 | 107.0392 | 1 | 107.0392 | S/S | CY8697 | 100 |  | 1500 | 125 | 1.2 | 0.001 | 0.3 | 0.1 | 15 | Y | 0.106 | 128.4585 | 128.4585 | 128.4585 | 120 | 68.6166 | 55 | 1e-06 | 1.2 | -128.4585 | 1.4405 | 55.26 |  | 28.26 | 12 | 15 | 0.51626 | [9 empty] | 3000 | 19339
BD | 1 | 1 | 1 | 1 | 100.7081 | 100.7081 | 1 | 100.7081 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 110.9215 | 110.9215 | 110.9215 | 120 | 66.7577 | 55 | 0.002 | 0.9 | -110.9215 | 1.6974 | 53.26 |  | 28.26 | 12 | 13 | 0.52886 | [9 empty] | 3500 | 23280
BD | 1 | 1 | 1 | 1 | 209.5192 | 209.5192 | 1 | 209.5192 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 13 | Y | 0.11 | 230.7692 | 230.7692 | 230.7692 | 145 | 80.3846 | 55 | 0.0012 | 0.85 | -230.7692 | 1.8302 | 66.55 |  | 24.55 | 12 | 30 | 0.31763 | [9 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 375.0812 | 375.0812 | 1 | 375.0812 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 13 | Y | 0.11 | 290.3226 | 290.3226 | 290.3226 | 145 | 86.9355 | 55 | 0.00032 | 0.654 | -290.3226 | 0.79933 | 111.55 |  | 24.55 | 12 | 75 | 0.2974 | [9 empty] | 4500 | 29407
BD | 1 | 1 | 1 | 1 | 527.3801 | 527.3801 | 1 | 527.3801 | S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 13 | Y | 0.11 | 461.5385 | 461.5385 | 461.5385 | 145 | 105.7692 | 55 | 0.000243 | 0.747 | -461.5385 | 1.0066 | 128.55 |  | 24.55 | 12 | 92 | 0.24375 | [9 empty] | 5000 | verify data
BD | 1 | 1 | 1 | 1 | 940.7559 | 940.7559 | 1 | 940.7559 | S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 15 | Y | 0.106 | 647.482 | 647.482 | 647.482 | 145 | 123.6331 | 55 | 5.98e-05 | 0.632 | -647.482 | 0.5543 | 385.26 |  | 28.26 | 12 | 345 | 0.40952
BD | 1 | 1 | 1 | 1 | 83.3275 | 83.3275 | 1 | 83.3275 | S/S | CY8697 | 100 |  | 1500 | 125 | 1.2 | 0.001 | 0.3 | 0.1 | 15 | N | 0.25 | 100 | 100 | 100 | 120 | 80 | 55 | 1e-06 | 1.2 | -100 | 1.4404 | 43.26 |  | 28.26 | 0 | 15 | 0.51916
BD | 1 | 1 | 1 | 1 | 73.17 | 73.17 | 1 | 73.17 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | N | 0.369 | 76.5607 | 76.5607 | 76.5607 | 120 | 83.2509 | 55 | 0.002 | 0.9 | -76.5607 | 1.4225 | 29.35 |  | 16.35 | 0 | 13 | 0.40112
BD | 1 | 1 | 1 | 1 | 98.4373 | 98.4373 | 1 | 98.4373 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 6.5 | Y | 0.122 | 107.9734 | 107.9734 | 107.9734 | 120 | 68.1728 | 55 | 0.002 | 0.9 | -107.9734 | 1.6738 | 41.35 |  | 16.35 | 12 | 13 | 0.42006
BD | 1 | 1 | 1 | 1 | 80.5948 | 80.5948 | 1 | 80.5948 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | N | 0.28 | 85.5263 | 85.5263 | 85.5263 | 120 | 78.9474 | 55 | 0.002 | 0.9 | -85.5263 | 1.4942 | 32.86 |  | 19.86 | 0 | 13 | 0.40772
BD | 1 | 1 | 1 | 1 | 99.4177 | 99.4177 | 1 | 99.4177 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 10 | Y | 0.115 | 109.2437 | 109.2437 | 109.2437 | 120 | 67.563 | 55 | 0.002 | 0.9 | -109.2437 | 1.6839 | 44.86 |  | 19.86 | 12 | 13 | 0.45123
BD | 1 | 1 | 1 | 1 | 82.9654 | 82.9654 | 1 | 82.9654 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | N | 0.255 | 88.4354 | 88.4354 | 88.4354 | 120 | 77.551 | 55 | 0.002 | 0.9 | -88.4354 | 1.5175 | 37.55 |  | 24.55 | 0 | 13 | 0.4526
BD | 1 | 1 | 1 | 1 | 100.1304 | 100.1304 | 1 | 100.1304 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 13 | Y | 0.11 | 110.1695 | 110.1695 | 110.1695 | 120 | 67.1186 | 55 | 0.002 | 0.9 | -110.1695 | 1.6914 | 49.55 |  | 24.55 | 12 | 13 | 0.49485
BD | 1 | 1 | 1 | 1 | 83.4567 | 83.4567 | 1 | 83.4567 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | N | 0.25 | 89.0411 | 89.0411 | 89.0411 | 120 | 77.2603 | 55 | 0.002 | 0.9 | -89.0411 | 1.5223 | 41.26 |  | 28.26 | 0 | 13 | 0.49439
BD | 1 | 1 | 1 | 1 | 100.7081 | 100.7081 | 1 | 100.7081 | S/S | F1892Dxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.106 | 110.9215 | 110.9215 | 110.9215 | 120 | 66.7577 | 55 | 0.002 | 0.9 | -110.9215 | 1.6974 | 53.26 |  | 28.26 | 12 | 13 | 0.52886
BD | 1 | 1 | 1 | 1 | 136.7472 | 136.7472 | 1 | 136.7472 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 6.5 | N | 0.369 | 138.6749 | 138.6749 | 138.6749 | 145 | 106.171 | 55 | 0.0012 | 0.85 | -138.6749 | 1.3881 | 46.35 |  | 16.35 | 0 | 30 | 0.33895
BD | 1 | 1 | 1 | 1 | 204.404 | 204.404 | 1 | 204.404 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 6.5 | Y | 0.122 | 223.8806 | 223.8806 | 223.8806 | 145 | 82.3134 | 55 | 0.0012 | 0.85 | -223.8806 | 1.7971 | 58.35 |  | 16.35 | 12 | 30 | 0.28546
BD | 1 | 1 | 1 | 1 | 155.1099 | 155.1099 | 1 | 155.1099 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 10 | N | 0.28 | 160.7143 | 160.7143 | 160.7143 | 145 | 100 | 55 | 0.0012 | 0.85 | -160.7143 | 1.4939 | 49.86 |  | 19.86 | 0 | 30 | 0.32145
BD | 1 | 1 | 1 | 1 | 161.2176 | 161.2176 | 1 | 161.2176 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 13 | N | 0.255 | 168.2243 | 168.2243 | 168.2243 | 145 | 97.8972 | 55 | 0.0012 | 0.85 | -168.2243 | 1.53 | 54.55 |  | 24.55 | 0 | 30 | 0.33836
BD | 1 | 1 | 1 | 1 | 162.499 | 162.499 | 1 | 162.499 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 15 | N | 0.25 | 169.8113 | 169.8113 | 169.8113 | 145 | 97.4528 | 55 | 0.0012 | 0.85 | -169.8113 | 1.5376 | 58.26 |  | 28.26 | 0 | 30 | 0.35853
BD | 1 | 1 | 1 | 1 | 218.4946 | 218.4946 | 1 | 218.4946 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 6.5 | N | 0.369 | 158.1722 | 158.1722 | 158.1722 | 145 | 113.3656 | 55 | 0.00032 | 0.654 | -158.1722 | 0.63018 | 91.35 |  | 16.35 | 0 | 75 | 0.41809
BD | 1 | 1 | 1 | 1 | 254.9045 | 254.9045 | 1 | 254.9045 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 10 | N | 0.28 | 187.5 | 187.5 | 187.5 | 145 | 107.5 | 55 | 0.00032 | 0.654 | -187.5 | 0.66772 | 94.86 |  | 19.86 | 0 | 75 | 0.37214
BD | 1 | 1 | 1 | 1 | 267.4506 | 267.4506 | 1 | 267.4506 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 13 | N | 0.255 | 197.8022 | 197.8022 | 197.8022 | 145 | 105.4396 | 55 | 0.00032 | 0.654 | -197.8022 | 0.6809 | 99.55 |  | 24.55 | 0 | 75 | 0.37222
BD | 1 | 1 | 1 | 1 | 270.1113 | 270.1113 | 1 | 270.1113 | S/S | ND41xx35 | 350 | 550 | 7340 | 150 | 0.654 | 0.32 | 0.14 | 0.06 | 15 | N | 0.25 | 200 | 200 | 200 | 145 | 105 | 55 | 0.00032 | 0.654 | -200 | 0.68372 | 103.26 |  | 28.26 | 0 | 75 | 0.38229
BD | 1 | 1 | 1 | 1 | 536.9916 | 536.9916 | 1 | 536.9916 | S | LS41xx60 | 600 | 950 | 19000 | 150 | 0.747 | 0.243 | 0.065 | 0.02 | 15 | Y | 0.106 | 471.2042 | 471.2042 | 471.2042 | 145 | 104.9476 | 55 | 0.000243 | 0.747 | -471.2042 | 1.016 | 132.26 |  | 28.26 | 12 | 92 | 0.2463
BD | 1 | 1 | 1 | 1 | 481.2811 | 481.2811 | 1 | 481.2811 | S | PS41xx25 | 2500 | 3925 | 48400 | 150 | 0.632 | 0.0598 | 0.024 | 0.009 | 15 | N | 0.25 | 318.0212 | 318.0212 | 318.0212 | 145 | 134.5053 | 55 | 5.98e-05 | 0.632 | -318.0212 | 0.47549 | 373.26 |  | 28.26 | 0 | 345 | 0.77556
BD | 1 | 1 | 1 | 1 | 317.5096 | 317.5096 | 1 | 317.5096 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.25 | 229.682 | 229.682 | 229.682 | 120 | 112.4205 | 55 | 0.000102 | 0.691 | -229.682 | 0.57119 | 218.26 |  | 28.26 | 0 | 190 | 0.68741
BD | 1 | 1 | 1 | 1 | 317.5096 | 317.5096 | 1 | 317.5096 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | N | 0.25 | 229.682 | 229.682 | 229.682 | 120 | 112.4205 | 55 | 0.000102 | 0.691 | -229.682 | 0.57119 | 218.26 |  | 28.26 | 0 | 190 | 0.68741
BD | 1 | 1 | 1 | 1 | 319.0299 | 319.0299 | 1 | 319.0299 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 6.5 | Y | 0.122 | 319.1489 | 319.1489 | 319.1489 | 145 | 93.9362 | 55 | 0.00044 | 0.86 | -319.1489 | 1.3013 | 82.55 |  | 16.35 | 12 | 54.2 | 0.25875 | [9 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 326.1319 | 326.1319 | 1 | 326.1319 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 10 | Y | 0.115 | 327.2727 | 327.2727 | 327.2727 | 145 | 92.6364 | 55 | 0.00044 | 0.86 | -327.2727 | 1.3156 | 86.06 |  | 19.86 | 12 | 54.2 | 0.26388 | [9 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 331.4051 | 331.4051 | 1 | 331.4051 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 13 | Y | 0.11 | 333.3333 | 333.3333 | 333.3333 | 145 | 91.6667 | 55 | 0.00044 | 0.86 | -333.3333 | 1.3263 | 90.75 |  | 24.55 | 12 | 54.2 | 0.27383 | [9 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 335.7504 | 335.7504 | 1 | 335.7504 | S/S | VSKE320-12 | 320 | 502 | 8500 | 150 | 0.86 | 0.44 | 0.125 | 0.035 | 15 | Y | 0.106 | 338.3459 | 338.3459 | 338.3459 | 145 | 90.8647 | 55 | 0.00044 | 0.86 | -338.3459 | 1.3351 | 94.46 |  | 28.26 | 12 | 54.2 | 0.28134 | [9 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 209.5192 | 209.5192 | 1 | 209.5192 | S/S | CS61xx16B | 160 | 250 | 3350 | 150 | 0.85 | 1.2 | 0.18 | 0.1 | 13 | Y | 0.11 | 230.7692 | 230.7692 | 230.7692 | 145 | 80.3846 | 55 | 0.0012 | 0.85 | -230.7692 | 1.8302 | 66.55 |  | 24.55 | 12 | 30 | 0.31763 | [9 empty] | 4000 | 26068
BD | 1 | 1 | 1 | 1 | 282.4985 | 282.4985 | 1 | 282.4985 | S/S | VSKE250-12 | 250 | 393 | 5900 | 150 | 0.92 | 0.49 | 0.16 | 0.035 | 15 | Y | 0.106 | 299.0033 | 299.0033 | 299.0033 | 145 | 86.6944 | 55 | 0.00049 | 0.92 | -299.0033 | 1.4324 | 86.36 |  | 28.26 | 12 | 46.1 | 0.3057 | [9 empty] | 4000 | 26068
3 | 6 | 1 | 6 | 3 | 171.9041 | 57.3014 | 1.7321 | 99.2489 | S/S | F1892SDxxxx | 90 | 150 | 1950 | 125 | 0.9 | 2 | 0.28 | 0.2 | 15 | Y | 0.072 | 71.2719 | 427.6316 | 427.6316 | 120 | 85.7895 | 55 | 0.006 | 0.9 | -71.2719 | 2.5205 | 79.26 |  | 28.26 | 12 | 39 | 0.46107 |  | 85.9521 | F1892Dxxxx | 309.4274 | 350 | 1724 | 2.036 | F1892Sxxxx |  | 60 | 269
[5 empty] | 150 | [32 empty] | 270 | 75 |  | 270 | 300 | 1324 | 2 | F1892Sxxxx
3 | 6 | 1 | 6 | 3 | 231.8976 | 77.2992 | 1.7321 | 133.8862 | S/S | CD63xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 15 | Y | 0.072 | 92.5926 | 555.5556 | 555.5556 | 120 | 95 | 55 | 0.0045 | 0.85 | -92.5926 | 2.3892 | 148.26 |  | 28.26 | 12 | 108 | 0.63933 |  | 115.9488 | CS61xx16B | 417.4158 | 450 | 2578 | 1.9405 | CS61xx16B |  | 125 | 510
[5 empty] | 225 | [27 empty] | 0.65893 |  |  |  |  | 405 | 112.5 | CS61xx16B | 405 | 450 | 2578 | 2 | CS61xx16B
3 | 6 | 1 | 6 | 3 | 308.3531 | 102.7844 | 1.7321 | 178.0278 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.072 | 102.8481 | 617.0886 | 617.0886 | 120 | 99.4304 | 55 | 0.001767 | 0.819 | -102.8481 | 1.3977 | 265.26 |  | 28.26 | 12 | 225 | 0.86025 |  | 154.1766 | VSKE250-12 | 555.0356 | 600 | 3532 | 1.9458 | ND41xx35 |  | 250 | 1058
[5 empty] | 330 | [27 empty] | 0.80382 |  |  |  |  | 594 | 165 | VSKE250-12 |  | 600 | 3532 | 1.8182 | VSKE320-12
3 | 6 | 3 | 2 | 1 | 439.1851 | 146.395 | 1.7321 | 253.5636 | S/S | ND43xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 15 | Y | 0.106 | 157.767 | 315.534 | 946.6019 | 120 | 88.4466 | 55 | 0.001767 | 0.819 | -157.767 | 1.7859 | 345.78 |  | 84.78 | 36 | 225 | 0.78732 |  | 219.5925 | VSKE250-12 | 790.5331 | 800 | 4196 | 1.8216 | LS41xx60 |  | 275 | 1196
[5 empty] | 500 | [27 empty] | 0.69156 |  |  |  |  | 900 | 250 | VSKE250-12 |  | 900 | 4708 | 1.8 | LS41xx60
3 | 6 | 3 | 2 | 1 | 645.8075 | 215.2692 | 1.7321 | 372.8572 | S/S | LD43xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 15 | Y | 0.106 | 218.8552 | 437.7104 | 1313.1313 | 120 | 101.3973 | 55 | 0.00096 | 0.81 | -218.8552 | 1.4965 | 525.78 |  | 84.78 | 36 | 405 | 0.81414 |  | 322.9038 | VSKE320-12 | 1162.4536 | 1200 | 7286 | 1.8581 | LS41xx60 |  | 500 | 2839
[5 empty] | 700 | [27 empty] | 0.75111 |  |  |  |  | 1260 | 350 | VSKE320-12 |  | 1500 | 10000 | 2.1429 | LS41xx60 | x2???
[47 empty] | 550 | 3110
3 | 6 | 3 | 2 | 1 | 796.9136 | 265.6379 | 1.7321 | 460.0983 | S/S | PD43xx07 | 700 | 1100 | 36500 | 125 | 0.703 | 0.184 | 0.058 | 0.018 | 15 | Y | 0.106 | 225.6944 | 451.3889 | 1354.1667 | 120 | 102.8472 | 55 | 0.000552 | 0.703 | -225.6944 | 0.99254 | 1095.78 |  | 84.78 | 36 | 975 | 1.375 |  | 398.4568 | LS41xx60 | 1434.4444 | 1500 | 10000 | 1.8823 |  |  | 700 | 3677
[5 empty] | 850 | [27 empty] | 1.2892 |  |  |  |  | 1530 | 425 | LS41xx60 |  | 1600 | 10900 | 1.8824
[47 empty] | 800 | 4196
3 | 6 | 6 | 1 | 1 | 1635.4136 | 545.1379 | 1.7321 | 944.2065 | S | PS43xx15 | 1500 | 2355 | 62000 | 125 | 0.691 | 0.102 | 0.024 | 0.009 | 15 | Y | 0.106 | 467.6259 | 467.6259 | 2805.7554 | 120 | 104.5683 | 55 | 0.000306 | 0.691 | -467.6259 | 1.0499 | 1381.56 |  | 169.56 | 72 | 1140 | 0.84478 |  | 817.7068 | 545.1379 | 2943.7444 | 3000 | 19339 | 1.8344 |  |  | 1500 | 10000
[5 empty] | 1750 | [27 empty] | 0.78946 |  |  |  |  | 3150 | 875 |  |  | 3500 | 23280 | 2
1 phase systems
1 | 4 | 1 | 4 | 2 | 189.2046 | 94.6023 | 1.4142 | 133.7878 | S/D | CD62xx15B | 160 | 250 | 4100 | 125 | 0.85 | 1.5 | 0.17 | 0.1 | 13 | Y | 0.084 | 107.2607 | 429.0429 | 429.0429 | 120 | 91.0396 | 55 | 0.003 | 0.85 | -107.2607 | 2.0096 | 108.55 |  | 24.55 | 12 | 72 | 0.57372 |  | 94.6023 | F1892Dxxxx | 340.5682 | 400 | 1984 | 2.1141 | CS61xx16B |  | 175 | 775
[5 empty] | 200 | [27 empty] | 0.54275 |  |  |  |  | 360 | 100
1 | 4 | 1 | 4 | 2 | 250.875 | 125.4375 | 1.4142 | 177.3954 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.084 | 121.2687 | 485.0746 | 485.0746 | 120 | 95.7463 | 55 | 0.001178 | 0.819 | -121.2687 | 1.2422 | 186.55 |  | 24.55 | 12 | 150 | 0.7436 |  | 125.4375 | 83.625 | 451.5751 | 500 | 2839 | 1.993 | CS61xx16B |  | 300 | 1324
[5 empty] | 250 | [32 empty] | 450 | 125
1 | 4 | 2 | 2 | 1 | 309.1813 | 154.5907 | 1.4142 | 218.6242 | S/D | ND42xx25 | 250 | 393 | 8800 | 125 | 0.819 | 0.589 | 0.14 | 0.06 | 13 | Y | 0.11 | 154.7619 | 309.5238 | 619.0476 | 120 | 89.0476 | 55 | 0.001178 | 0.819 | -154.7619 | 1.4 | 223.1 |  | 49.1 | 24 | 150 | 0.72158 |  | 154.5907 | 103.0604 | 556.5263 | 600 | 3532 | 1.9406 | ND41xx35 |  | 350 | 1724
[5 empty] | 325 | [32 empty] | 585 | 162.5
1 | 4 | 2 | 2 | 1 | 447.2013 | 223.6006 | 1.4142 | 316.2191 | S/S | LD42xx50 | 500 | 900 | 16300 | 125 | 0.81 | 0.32 | 0.065 | 0.02 | 13 | Y | 0.11 | 213.1148 | 426.2295 | 852.459 | 120 | 101.8852 | 55 | 0.00064 | 0.81 | -213.1148 | 1.2017 | 343.1 |  | 49.1 | 24 | 270 | 0.76722 |  | 223.6006 | 149.0671 | 804.9623 | 800 | 4196 | 1.7889 | ND41xx35 |  | 450 | 2578
[5 empty] | 450 | [32 empty] | 810 | 225

## SCR ASSEMBLIES-PRODUCTION
3Φ-1Φ-BD-FWD |  |  | Includes safety factor on Tj | Device Parameters |  |  | Operational Conditions
Circuit Type | Number of HS250 | Number of Modules/HS | IdcMax | Device Part No | Idave Max | Ifsm | HS250 length | Fan | Pt/HS =nsxPd | Pt =nsxPd | Ts | Ta | [6 empty] | FWD | FUSE A30QS | BD
|  |  | (A) |  | (A) | (A) | (") |  | (W) | (W) | (°C) | (°C) | TOTAL |  | HS250 | FAN | MODULE | $/(A) |  | (A)
3 | 1 | 3 | 150 | F1892SDxxxx | 90 | 1950 | 15 | Y | 427.6316 | 427.6316 | 85.7895 | 55 | 79.26 |  | 28.26 | 12 | 39 | 0.46107 | F1892Dxxxx | 300 | F1892Sxxxx
3 | 1 | 3 | 225 | CD63xx15B | 160 | 4100 | 15 | Y | 555.5556 | 555.5556 | 95 | 55 | 148.26 |  | 28.26 | 12 | 108 | 0.63933 | CS61xx16B | 450 | CS61xx16B
[14 empty] | 0.65893 |  |  |  |  | CS61xx16B |  | CS61xx16B
3 | 1 | 3 | 325 | ND43xx25 | 250 | 8800 | 15 | Y | 617.0886 | 617.0886 | 99.4304 | 55 | 265.26 |  | 28.26 | 12 | 225 | 0.86025 | VSKE250-12 | 600 | ND41xx35
[14 empty] | 0.80382 |  |  |  |  | VSKE250-12 |  | VSKE320-12
3 | 3 | 1 | 500 | ND43xx25 | 250 | 8800 | 15 | Y | 315.534 | 946.6019 | 88.4466 | 55 | 345.78 |  | 84.78 | 36 | 225 | 0.78732 | VSKE250-12 | 900 | LS41xx60
3 | 3 | 1 | 645.8075 | LD43xx50 | 500 | 16300 | 15 | Y | 437.7104 | 1313.1313 | 101.3973 | 55 | 525.78 |  | 84.78 | 36 | 405 | 0.81414 | VSKE320-12 | 1500 | LS41xx60 | x2???
3 | 3 | 1 | 796.9136 | PD43xx07 | 700 | 36500 | 15 | Y | 451.3889 | 1354.1667 | 102.8472 | 55 | 1095.78 |  | 84.78 | 36 | 975 | 1.375 | LS41xx60 | 1600
3 | 6 | 1 | 1635.4136 | PS43xx15 | 1500 | 62000 | 15 | Y | 467.6259 | 2805.7554 | 104.5683 | 55 | 1381.56 |  | 169.56 | 72 | 1140 | 0.84478 |  | 3500
1 phase systems
1 | 1 | 2 | 200 | CD62xx15B | 160 | 4100 | 13 | Y | 429.0429 | 429.0429 | 91.0396 | 55 | 108.55 |  | 24.55 | 12 | 72 | 0.57372 | F1892Dxxxx | 400 | CS61xx16B
0.54275
1 | 1 | 2 | 250 | ND42xx25 | 250 | 8800 | 13 | Y | 485.0746 | 485.0746 | 95.7463 | 55 | 186.55 |  | 24.55 | 12 | 150 | 0.7436 | 83.625 | 500 | CS61xx16B
1 | 2 | 1 | 325 | ND42xx25 | 250 | 8800 | 13 | Y | 309.5238 | 619.0476 | 89.0476 | 55 | 223.1 |  | 49.1 | 24 | 150 | 0.72158 | 103.0604 | 600 | ND41xx35
1 | 2 | 1 | 450 | LD42xx50 | 500 | 16300 | 13 | Y | 426.2295 | 852.459 | 101.8852 | 55 | 343.1 |  | 49.1 | 24 | 270 | 0.76722 | 149.0671 | 800 | ND41xx35

## TX Short Circuit
Transformer Short Circuit Current Capability Calculation
Exemple:
TX: 28kVA, 3ph, Vsec=127V (line-line), impedance = 5.75%
1/0.0575 = 17.4
I = 28000/(127*1.732) = 127.3A (on The Secondary)
Isc= 127.3 x 17.4 = 2215A (on The Secondary)
Automatic Calculation
|  |  | S (kA) | Vsec | Z (imp)
| Input Value |  | 3.5 | 127 | 0.033
| Result | Isc | 482.73

## Capacitor Discharge
Capacitor Discharge Current
Capacitor energy = ½ CV2 (j)
Capacitor discharge Current = CV/t (A)
Capacitor discharge Current @ 10 ms = CV/0.01 (A)

## Capacitor Service Life
Electrolytic Capacitor Service Life | [7 empty] | To、Lo、保証寿命、温度上昇設定値
[9 empty] | 周囲温度 | HCG7 | HCGH (～250WV) | HCGH (400WV) | HCGF5/6 | FXA/FX2 | GXA/GX2 | HXA | FXR | GXR | GXH
[8 empty] | 各温度毎の中心部温度上昇設定値（K） | 40 | 21 | 31 | 35 | 31 | 35 | 35 | 35 | 40 | 40 | -
[9 empty] | 60(55) | 15 | 22 | 30 | 19 | 25 | 25 | 25 | 30 | 33 | 35
L = L0 x 2(T0-T)/10 x (VW/V)2.5 |  |  |  | If V/WV<0.6, use V/WV = 0.6. |  |  |  |  | 70 | - | 12.5 | 15 | 12.5 | - | - | - | - | - | -
T = Ta + ΔT0 x (I/IR)2 | [8 empty] | 85 | 5 | 5 | 8.5 | 5 | 8.5 | 20 | 5 | 10 | 26 | 25
[9 empty] | 105 | - | 2 | 5 | - | - | 5 | - | - | 6.5 | 10
L | Estimated Life Time | [6 empty] | To（℃） |  | 90 | 107 | 110 | 90 | 93.5 | 110 | 90 | 95 | 111.5 | 115
L0 | Stadard Life Time (Given in the Data Sheet) | [6 empty] | Lo（h） |  | 4000 | 4000 | 4000 | 4000 | 8000 | 8000 | 20000 | 8000 | 8000 | 8000
T0 | Maximum Capacitor Core Temperature / Hot Spot (Given in the Data Sheet) | [6 empty] | 保証寿命（h） |  | 2000 | 2000 | 2000 | 2000 | 5000 | 5000 | 20000 | 5000 | 5000 | 5000
Note: this value is given for Maximum Ripple Current and Maximum Operating Temperature
T | Actual Capacitor Core Temperature @ Actual Temperature Ta and Ripple Current | [6 empty] | リプル補正係数（ただし、04年カタログ記載値をベースとする）
Ta | Actual Ambient Temperature
ΔT0 | Maximum Capacitor Core temperature increase | [6 empty] | （周波数） |  | 50/60 | 120 | 300 | 1K | ≧10K
I | Actual Ripple Curent @ Ta and given Ripple Frequency | [6 empty] | HCG7 |  | 0.8 | 1 | 1.1 | 1.3 | 1.4
IR | Maximum allowable Ripple Curent @ Ta and given Ripple Frequency | [6 empty] | HCGH |  | 0.8 | 1 | 1.1 | 1.3 | 1.4
Ir | Maximum Ripple Current at 40°C,120Hz (Given in Data Sheet) | [6 empty] | HCGF5 |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
[8 empty] | HCGF6 |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
V |  | 350 | (V) |  |  |  |  | FXA |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
I |  | 14 | (A) |  |  |  |  | FX2 |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
Ta |  | 40 | (°C) |  |  |  |  | GXA |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
WV |  | 400 | (V) | Data Sheet |  |  |  | GX2 |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
L0 |  | 4000 | (hrs) | Data Sheet |  |  |  | HXA |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
T0 |  | 90 | (°C) | Data Sheet | 31 |  |  | FXR |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
ΔT0 |  | 31 | (°K) | Data Sheet |  |  |  | GXR |  | 0.7 | 1 | 1.1 | 1.3 | 1.4
Ir |  | 22.2 | (A) | Data Sheet
Ta Correction Factor |  | 1 |  | Data Sheet | 1 |  |  | （周囲温度） |  | 40 | 60 | 70 | 85 | 105
Frequency Correction Factor |  | 1.1 |  | Data Sheet |  |  |  | HCG7 |  | 1 | 0.81 | - | 0.62 | -
IR |  | 24.42 |  | Computed Value |  |  |  | HCGH(～250WV) |  | 4.9 | (55℃) 3.9 | 3 | 1.8 | 1
T |  | 50.1889 | (°C) | Computed Value |  |  |  | HCGF5 |  | 1 | 0.75 | 0.62 | 0.37 | -
L |  | 88201.0972 | (hrs) | Computed Value |  |  |  | FXA |  | 1.89 | 1.67 | - | 1 | -
|  | 3675.0457 | days |  |  |  |  | FX2 |  | 1.89 | 1.67 | - | 1 | -
|  | 10.0686 | years |  |  |  |  | GXA |  | 2.44 | 2.16 | - | 2 | 1
[8 empty] | GX2 |  | 2.44 | 2.16 | - | 2 | 1
[8 empty] | HXA |  | 2.44 | 2.16 | - | 1 | -
[8 empty] | FXR |  | 1.89 | 1.67 | - | 1 | -
[8 empty] | GXR |  | 2.44 | 2.16 | - | 2 | 1
V |  | 300 | (V) |  |  |  | V |  | 135 | (V)
I |  | 9 | (A) |  |  |  | I |  | 15 | (A)
Ta |  | 55 | (°C) |  |  |  | Ta |  | 55 | (°C)
WV |  | 450 | (V) | Data Sheet |  | 1.5 | WV |  | 200 | (V) | Data Sheet
L0 |  | 4000 | (hrs) | Data Sheet |  |  | L0 |  | 4000 | (hrs) | Data Sheet
T0 |  | 90 | (°C) | Data Sheet |  |  | T0 |  | 90 | (°C) | Data Sheet
ΔT0 |  | 19 | (°K) | Data Sheet |  |  | ΔT0 |  | 19 | (°K) | Data Sheet
Ir |  | 15.8 | (A) | Data Sheet |  |  | Ir |  | 28 | (A) | Data Sheet
Ta Correction Factor |  | 0.75 |  | Data Sheet |  |  | Ta Correction Factor |  | 0.75 |  | Data Sheet
Frequency Correction Factor |  | 1.1 |  | Data Sheet |  |  | Frequency Correction Factor |  | 1.1 |  | Data Sheet
IR |  | 13.035 |  | Computed Value |  |  | IR |  | 23.1 |  | Computed Value
T |  | 64.0577 | (°C) | Computed Value |  |  | T |  | 63.0115 | (°C) | Computed Value |  | -8.0115
L |  | 66562.5656 | (hrs) | Computed Value | 832.0321 |  | L |  | 69380.3194 | (hrs) | Computed Value
|  | 2773.4402 | days | [5 empty] | 2890.8466 | days |  |  | 175200
|  | 7.5985 | years | [5 empty] | 7.9201 | years